## Input
Bio2 climate-equipment control inputs
Generated from Bio2-Controls-Inventory-29Jan2026.xlsx. Rows are candidate manipulated controls, setpoints, and actuator outputs; uncertain equipment mappings are flagged for engineering review.
Physical quantity / setting | Physical symbol | Control family | Manipulated signal type | Confidence | Affected biome | Biome/equipment note | Equipment tag | Equipment description / lookup | BMS path (ID_NAME) | Device measurement | Expanded measurement / meaning | Physical climate effect | PDE / inverse-problem role | How it enters PDE or inverse problem | Source system | Inventory file | Inventory sheet | Inventory ID | Oracle owner | Oracle table | Oracle selector / WHERE key | Time column | Value column | Raw unit | SI / normalized unit | Formula for conversion | Inventory category | Value facets / BACnet range | Inventory variable description | Availability start | Availability end | Value count | Live-tested in Oracle? | Concrete SQL query for calendar year 2025 | Mirror fallback | Engineering verification notes
Cooling valve command | u_AHUR1_CCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR1 | Rainforest air-handling unit AHUR1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR1_CCVlvCmd | CCVlvCmd | CCVlv Cmd; Cmd=Command; Vlv=Valve | Changes cooling capacity available to Rainforest or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 941 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR1_CCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-08 | present | 150421 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_CCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_CCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR1_CCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUR1_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR1 | Rainforest air-handling unit AHUR1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR1_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to Rainforest or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 925 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR1_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-08 | present | 150421 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR1_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUR1_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR1 | Rainforest air-handling unit AHUR1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR1_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 942 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR1_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR1_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUR1_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR1 | Rainforest air-handling unit AHUR1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR1_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 939 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR1_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR1_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUR1_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR1 | Rainforest air-handling unit AHUR1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR1_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 940 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR1_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR1_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Heating valve command | u_AHUR1_HCVlvCmd | Heating valve command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR1 | Rainforest air-handling unit AHUR1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR1_HCVlvCmd | HCVlvCmd | HotwaterControlVlvCommand | Changes heating capacity available to Rainforest or to the shared hot-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 935 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR1_HCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-08 | present | 150421 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_HCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_HCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR1_HCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Heating valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUR1_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR1 | Rainforest air-handling unit AHUR1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR1_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting Rainforest; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 931 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR1_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 1072 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR1_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUR1_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR1 | Rainforest air-handling unit AHUR1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR1_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 927 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR1_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 730 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR1_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUR1_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR1 | Rainforest air-handling unit AHUR1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR1_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Rainforest. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 936 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR1_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR1_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUR1_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR1 | Rainforest air-handling unit AHUR1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR1_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving Rainforest. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 933 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR1_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR1_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUR1_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR1 | Rainforest air-handling unit AHUR1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR1_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Rainforest. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 929 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR1_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-08 | present | 150421 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR1_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUR1_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR1 | Rainforest air-handling unit AHUR1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR1_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Rainforest. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 934 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR1_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR1_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR1_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUR2_CCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR2 | Rainforest air-handling unit AHUR2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR2_CCVlvCmd | CCVlvCmd | CCVlv Cmd; Cmd=Command; Vlv=Valve | Changes cooling capacity available to Rainforest or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 926 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR2_CCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-08 | present | 150421 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_CCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_CCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR2_CCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUR2_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR2 | Rainforest air-handling unit AHUR2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR2_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to Rainforest or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 910 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR2_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-08 | present | 150421 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR2_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUR2_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR2 | Rainforest air-handling unit AHUR2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR2_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 923 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR2_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR2_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUR2_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR2 | Rainforest air-handling unit AHUR2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR2_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 924 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR2_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR2_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUR2_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR2 | Rainforest air-handling unit AHUR2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR2_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 922 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR2_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR2_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Heating valve command | u_AHUR2_HCVlvCmd | Heating valve command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR2 | Rainforest air-handling unit AHUR2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR2_HCVlvCmd | HCVlvCmd | HotwaterControlVlvCommand | Changes heating capacity available to Rainforest or to the shared hot-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 920 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR2_HCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-08 | present | 150421 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_HCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_HCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR2_HCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Heating valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUR2_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR2 | Rainforest air-handling unit AHUR2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR2_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting Rainforest; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 916 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR2_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 1321 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR2_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUR2_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR2 | Rainforest air-handling unit AHUR2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR2_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 911 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR2_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 944 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR2_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUR2_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR2 | Rainforest air-handling unit AHUR2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR2_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Rainforest. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 918 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR2_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR2_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUR2_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR2 | Rainforest air-handling unit AHUR2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR2_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving Rainforest. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 917 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR2_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR2_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUR2_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR2 | Rainforest air-handling unit AHUR2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR2_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Rainforest. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 913 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR2_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR2_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUR2_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR2 | Rainforest air-handling unit AHUR2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR2_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Rainforest. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 915 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR2_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR2_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR2_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUR3_CCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR3 | Rainforest air-handling unit AHUR3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR3_CCVlvCmd | CCVlvCmd | CCVlv Cmd; Cmd=Command; Vlv=Valve | Changes cooling capacity available to Rainforest or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 908 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR3_CCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-08 | present | 150421 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR3_CCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR3_CCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR3_CCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUR3_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR3 | Rainforest air-handling unit AHUR3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR3_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to Rainforest or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 900 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR3_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-08 | present | 150421 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR3_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR3_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR3_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUR3_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR3 | Rainforest air-handling unit AHUR3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR3_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 906 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR3_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR3_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR3_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR3_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUR3_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR3 | Rainforest air-handling unit AHUR3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR3_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 907 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR3_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR3_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR3_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR3_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Heating valve command | u_AHUR3_HCVlvCmd | Heating valve command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR3 | Rainforest air-handling unit AHUR3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR3_HCVlvCmd | HCVlvCmd | HotwaterControlVlvCommand | Changes heating capacity available to Rainforest or to the shared hot-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 905 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR3_HCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-08 | present | 150421 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR3_HCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR3_HCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR3_HCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Heating valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUR3_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR3 | Rainforest air-handling unit AHUR3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR3_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting Rainforest; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 904 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR3_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 2833 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR3_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR3_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR3_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUR3_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR3 | Rainforest air-handling unit AHUR3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR3_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 901 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR3_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 2096 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR3_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR3_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR3_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Cooling valve command | u_AHUR4_CCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR4 | Rainforest air-handling unit AHUR4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR4_CCVlvCmd | CCVlvCmd | CCVlv Cmd; Cmd=Command; Vlv=Valve | Changes cooling capacity available to Rainforest or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 899 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR4_CCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_CCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_CCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR4_CCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUR4_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR4 | Rainforest air-handling unit AHUR4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR4_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to Rainforest or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 885 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR4_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-08 | present | 150421 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR4_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUR4_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR4 | Rainforest air-handling unit AHUR4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR4_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 898 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR4_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR4_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUR4_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR4 | Rainforest air-handling unit AHUR4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR4_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 897 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR4_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR4_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUR4_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR4 | Rainforest air-handling unit AHUR4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR4_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 896 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR4_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR4_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUR4_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR4 | Rainforest air-handling unit AHUR4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR4_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting Rainforest; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 891 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR4_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 3099 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR4_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUR4_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR4 | Rainforest air-handling unit AHUR4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR4_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 886 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR4_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 2772 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR4_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUR4_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR4 | Rainforest air-handling unit AHUR4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR4_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Rainforest. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 893 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR4_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR4_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUR4_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR4 | Rainforest air-handling unit AHUR4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR4_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving Rainforest. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 892 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR4_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR4_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUR4_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR4 | Rainforest air-handling unit AHUR4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR4_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Rainforest. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 888 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR4_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR4_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUR4_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR4 | Rainforest air-handling unit AHUR4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR4_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Rainforest. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 890 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR4_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR4_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR4_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUR5_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR5 | Rainforest air-handling unit AHUR5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR5_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to Rainforest or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 868 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR5_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-08 | present | 150421 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR5_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUR5_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR5 | Rainforest air-handling unit AHUR5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR5_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 883 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR5_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR5_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUR5_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR5 | Rainforest air-handling unit AHUR5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR5_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 882 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR5_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR5_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUR5_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR5 | Rainforest air-handling unit AHUR5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR5_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 881 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR5_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR5_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUR5_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR5 | Rainforest air-handling unit AHUR5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR5_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting Rainforest; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 875 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR5_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 3593 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR5_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUR5_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR5 | Rainforest air-handling unit AHUR5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR5_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 871 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR5_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | present | 3331 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR5_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUR5_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR5 | Rainforest air-handling unit AHUR5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR5_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Rainforest. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 878 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR5_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR5_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUR5_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR5 | Rainforest air-handling unit AHUR5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR5_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving Rainforest. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 877 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR5_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR5_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUR5_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR5 | Rainforest air-handling unit AHUR5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR5_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Rainforest. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 873 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR5_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR5_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUR5_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR5 | Rainforest air-handling unit AHUR5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR5_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Rainforest. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 876 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR5_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR5_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR5_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUR6_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR6 | Rainforest air-handling unit AHUR6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR6_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to Rainforest or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 854 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR6_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-08 | present | 150421 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR6_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUR6_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR6 | Rainforest air-handling unit AHUR6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR6_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 869 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR6_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR6_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUR6_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR6 | Rainforest air-handling unit AHUR6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR6_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 867 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR6_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR6_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUR6_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR6 | Rainforest air-handling unit AHUR6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR6_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 866 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR6_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR6_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUR6_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR6 | Rainforest air-handling unit AHUR6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR6_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting Rainforest; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 861 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR6_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 1643 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR6_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUR6_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR6 | Rainforest air-handling unit AHUR6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR6_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 856 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR6_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 1483 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR6_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUR6_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR6 | Rainforest air-handling unit AHUR6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR6_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Rainforest. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 863 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR6_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR6_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUR6_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR6 | Rainforest air-handling unit AHUR6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR6_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving Rainforest. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 862 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR6_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR6_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUR6_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR6 | Rainforest air-handling unit AHUR6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR6_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Rainforest. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 858 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR6_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR6_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUR6_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR6 | Rainforest air-handling unit AHUR6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR6_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Rainforest. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 860 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR6_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR6_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR6_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUR7_CCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR7 | Rainforest air-handling unit AHUR7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR7_CCVlvCmd | CCVlvCmd | CCVlv Cmd; Cmd=Command; Vlv=Valve | Changes cooling capacity available to Rainforest or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 853 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR7_CCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR7_CCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR7_CCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR7_CCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Supply fan command | u_AHUR7_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | AHUR7 | Rainforest air-handling unit AHUR7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUR7_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 850 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUR7_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-20 | 332 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUR7_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUR7_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUR7_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Damper control | u_MiscR1_DprCloseSp | Damper control | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscR1 | Rainforest damper/control-sensor setpoint group; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscR1_DprCloseSp | DprCloseSp | Dpr Close Sp | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 575 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCR1_DPRCLOSESP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:0 | Temperature | 2022-01-22 | present | 149090 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCR1_DPRCLOSESP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCR1_DPRCLOSESP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCR1_DPRCLOSESP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Damper control | u_MiscR1_DprOpenSp | Damper control | setpoint | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscR1 | Rainforest damper/control-sensor setpoint group; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscR1_DprOpenSp | DprOpenSp | DamperOpenSetpoint | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 572 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCR1_DPROPENSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:0 | Temperature | 2022-01-22 | present | 149090 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCR1_DPROPENSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCR1_DPROPENSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCR1_DPROPENSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Damper control | u_MiscRF1_RoofDmpCmd | Damper control | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscRF1 | Rainforest miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscRF1_RoofDmpCmd | RoofDmpCmd | Roof Dmp Cmd; Cmd=Command; Dmp=Damper | Changes ventilation path, outside-air fraction, or air exchange for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 558 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCRF1_ROOFDMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2022-01-06 | 2026-04-30 | 4147 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_ROOFDMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_ROOFDMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCRF1_ROOFDMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Damper control.
Fan / VFD speed control | u_MiscRF1_ExhFanCmd | Fan / VFD speed control | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscRF1 | Rainforest miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscRF1_ExhFanCmd | ExhFanCmd | Exh Fan Cmd; Cmd=Command; Exh=Exhaust | Changes airflow, exchange, pressure balance, or mixing for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 571 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCRF1_EXHFANCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-12-28 | 2026-05-01 | 2670 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_EXHFANCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_EXHFANCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCRF1_EXHFANCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control.
Fan / VFD speed control | u_MiscRF1_ExhFanSpd | Fan / VFD speed control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscRF1 | Rainforest miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscRF1_ExhFanSpd | ExhFanSpd | Exh Fan Spd; Exh=Exhaust; Spd=Speed | Changes airflow, exchange, pressure balance, or mixing for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 570 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCRF1_EXHFANSPD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; | Speed | 2022-01-22 | present | 149090 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_EXHFANSPD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_EXHFANSPD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCRF1_EXHFANSPD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Fan / VFD speed control | u_MiscRF1_InjFanCmd | Fan / VFD speed control | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscRF1 | Rainforest miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscRF1_InjFanCmd | InjFanCmd | Inj Fan Cmd; Cmd=Command; Inj=Injection | Changes airflow, exchange, pressure balance, or mixing for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 568 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCRF1_INJFANCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2022-01-30 | 2026-05-01 | 5056 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_INJFANCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_INJFANCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCRF1_INJFANCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control.
Fan / VFD speed control | u_MiscRF1_InjFanSpd | Fan / VFD speed control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscRF1 | Rainforest miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscRF1_InjFanSpd | InjFanSpd | Inj Fan Spd; Inj=Injection; Spd=Speed | Changes airflow, exchange, pressure balance, or mixing for Rainforest. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 566 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCRF1_INJFANSPD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; | Speed | 2022-01-08 | present | 150421 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_INJFANSPD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_INJFANSPD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCRF1_INJFANSPD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Solenoid valve / unknown valve | u_MiscRF1_SV57 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscRF1 | Rainforest miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscRF1_SV57 | SV57 | SV57 | Changes hydronic/air/water flow through equipment serving Rainforest. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 556 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCRF1_SV57 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-08 | 204 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV57 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV57 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCRF1_SV57 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscRF1_SV58 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscRF1 | Rainforest miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscRF1_SV58 | SV58 | SV58 | Changes hydronic/air/water flow through equipment serving Rainforest. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 555 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCRF1_SV58 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-08 | 210 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV58 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV58 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCRF1_SV58 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscRF1_SV59 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscRF1 | Rainforest miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscRF1_SV59 | SV59 | SV59 | Changes hydronic/air/water flow through equipment serving Rainforest. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 553 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCRF1_SV59 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-08 | 206 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV59 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV59 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCRF1_SV59 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscRF1_SV61 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscRF1 | Rainforest miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscRF1_SV61 | SV61 | SV61 | Changes hydronic/air/water flow through equipment serving Rainforest. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 554 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCRF1_SV61 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-30 | 9756 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV61 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV61 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCRF1_SV61 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscRF1_SV62 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscRF1 | Rainforest miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscRF1_SV62 | SV62 | SV62 | Changes hydronic/air/water flow through equipment serving Rainforest. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 552 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCRF1_SV62 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-30 | 9766 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV62 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV62 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCRF1_SV62 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscRF1_SV64 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscRF1 | Rainforest miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscRF1_SV64 | SV64 | SV64 | Changes hydronic/air/water flow through equipment serving Rainforest. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 551 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCRF1_SV64 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-30 | 9830 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV64 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV64 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCRF1_SV64 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscRF1_SV65 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscRF1 | Rainforest miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscRF1_SV65 | SV65 | SV65 | Changes hydronic/air/water flow through equipment serving Rainforest. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 550 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCRF1_SV65 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-08 | 206 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV65 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV65 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCRF1_SV65 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscRF1_SV66 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscRF1 | Rainforest miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscRF1_SV66 | SV66 | SV66 | Changes hydronic/air/water flow through equipment serving Rainforest. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 549 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCRF1_SV66 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-08 | 198 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV66 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV66 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCRF1_SV66 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscRF1_SV67 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscRF1 | Rainforest miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscRF1_SV67 | SV67 | SV67 | Changes hydronic/air/water flow through equipment serving Rainforest. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 547 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCRF1_SV67 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-08 | 208 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV67 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV67 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCRF1_SV67 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscRF1_SV82 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscRF1 | Rainforest miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscRF1_SV82 | SV82 | SV82 | Changes hydronic/air/water flow through equipment serving Rainforest. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 548 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCRF1_SV82 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-08 | 210 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV82 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCRF1_SV82 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCRF1_SV82 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Rain / irrigation control | u_MiscSAV1_RFRainFlwRat | Rain / irrigation control | needs engineering verification | Low - equipment meaning requires engineering verification | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscSAV1 | Rainforest rain/Tesco subsystem recorded under MiscSAV tag; verify exact equipment in BMS. | /UAB2_BIO1/B4000_MiscSAV1_RFRainFlwRat | RFRainFlwRat | RFRain Flw Rat; FlwRat=FlowRate; Flw=Flow | Changes water input or irrigation forcing for Rainforest. | Source-term control parameter | Use as prescribed water-input/source forcing or as a candidate manipulated variable in control/inversion. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 531 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_RFRAINFLWRAT | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | L/min | m^3/s | Q = VALUE * 1e-3 / 60 | SENSOR | units=u:liters per minute;L/min;(m3)(s-1);*1.6666666666666667E-5; | Flow rate | 2022-01-22 | present | 149090 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_RFRAINFLWRAT live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE * 1e-3 / 60 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_RFRAINFLWRAT t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_RFRAINFLWRAT | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Rain / irrigation control. Low - equipment meaning requires engineering verification
Rain / irrigation control | u_MiscSAV1_RFTescoOADprCmd | Rain / irrigation control | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscSAV1 | Rainforest rain/Tesco subsystem recorded under MiscSAV tag; verify exact equipment in BMS. | /UAB2_BIO1/B4000_MiscSAV1_RFTescoOADprCmd | RFTescoOADprCmd | RFTesco OADpr Cmd; Cmd=Command | Changes water input or irrigation forcing for Rainforest. | Source-term control parameter | Use as prescribed water-input/source forcing or as a candidate manipulated variable in control/inversion. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 530 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_RFTESCOOADPRCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149090 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_RFTESCOOADPRCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_RFTESCOOADPRCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_RFTESCOOADPRCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Rain / irrigation control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Rain / irrigation control | u_MiscSAV1_RFTescoVFDCmd | Rain / irrigation control | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscSAV1 | Rainforest rain/Tesco subsystem recorded under MiscSAV tag; verify exact equipment in BMS. | /UAB2_BIO1/B4000_MiscSAV1_RFTescoVFDCmd | RFTescoVFDCmd | RFTesco VFDCmd; Cmd=Command; VFD=Variable Frequency Drive | Changes water input or irrigation forcing for Rainforest. | Source-term control parameter | Use as prescribed water-input/source forcing or as a candidate manipulated variable in control/inversion. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 528 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_RFTESCOVFDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 141 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_RFTESCOVFDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_RFTESCOVFDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_RFTESCOVFDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Rain / irrigation control.
Rain / irrigation control | u_MiscSAV1_RFTescoVFDDirCmd | Rain / irrigation control | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscSAV1 | Rainforest rain/Tesco subsystem recorded under MiscSAV tag; verify exact equipment in BMS. | /UAB2_BIO1/B4000_MiscSAV1_RFTescoVFDDirCmd | RFTescoVFDDirCmd | RFTesco VFDDir Cmd; Cmd=Command; VFD=Variable Frequency Drive | Changes water input or irrigation forcing for Rainforest. | Source-term control parameter | Use as prescribed water-input/source forcing or as a candidate manipulated variable in control/inversion. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 526 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_RFTESCOVFDDIRCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:Exhaust¦falseText=s:Injection¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 134 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_RFTESCOVFDDIRCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_RFTESCOVFDDIRCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_RFTESCOVFDDIRCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Rain / irrigation control.
Rain / irrigation control | u_MiscSAV1_RFTescoVFDOut | Rain / irrigation control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscSAV1 | Rainforest rain/Tesco subsystem recorded under MiscSAV tag; verify exact equipment in BMS. | /UAB2_BIO1/B4000_MiscSAV1_RFTescoVFDOut | RFTescoVFDOut | RFTesco VFDOut; VFD=Variable Frequency Drive | Changes water input or irrigation forcing for Rainforest. | Source-term control parameter | Use as prescribed water-input/source forcing or as a candidate manipulated variable in control/inversion. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 525 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_RFTESCOVFDOUT | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149090 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_RFTESCOVFDOUT live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_RFTESCOVFDOUT t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_RFTESCOVFDOUT | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Rain / irrigation control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Rain / irrigation control | u_MiscSAV1_RFTescoVlvCmd | Rain / irrigation control | command | High - name is command/setpoint for named climate equipment | Rainforest | Inventory BIOM=1, BIOMNAME=Rainforest. | MiscSAV1 | Rainforest rain/Tesco subsystem recorded under MiscSAV tag; verify exact equipment in BMS. | /UAB2_BIO1/B4000_MiscSAV1_RFTescoVlvCmd | RFTescoVlvCmd | RFTesco Vlv Cmd; Cmd=Command; Vlv=Valve | Changes water input or irrigation forcing for Rainforest. | Source-term control parameter | Use as prescribed water-input/source forcing or as a candidate manipulated variable in control/inversion. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 524 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_RFTESCOVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 148 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_RFTESCOVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_RFTESCOVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_RFTESCOVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Rain / irrigation control.
Cooling valve command | u_AHUS1_CCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS1 | Savanna air-handling unit AHUS1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS1_CCVlvCmd | CCVlvCmd | CCVlv Cmd; Cmd=Command; Vlv=Valve | Changes cooling capacity available to Savanna or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 851 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS1_CCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_CCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_CCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS1_CCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUS1_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS1 | Savanna air-handling unit AHUS1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS1_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to Savanna or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 835 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS1_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS1_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS1_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS1 | Savanna air-handling unit AHUS1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS1_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 848 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS1_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS1_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS1_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS1 | Savanna air-handling unit AHUS1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS1_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 849 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS1_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS1_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS1_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS1 | Savanna air-handling unit AHUS1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS1_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 847 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS1_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS1_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Heating valve command | u_AHUS1_HCVlvCmd | Heating valve command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS1 | Savanna air-handling unit AHUS1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS1_HCVlvCmd | HCVlvCmd | HotwaterControlVlvCommand | Changes heating capacity available to Savanna or to the shared hot-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 844 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS1_HCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_HCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_HCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS1_HCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Heating valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUS1_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS1 | Savanna air-handling unit AHUS1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS1_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting Savanna; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 841 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS1_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 4263 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS1_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUS1_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS1 | Savanna air-handling unit AHUS1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS1_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 836 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS1_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 3629 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS1_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUS1_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS1 | Savanna air-handling unit AHUS1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS1_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 842 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS1_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS1_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUS1_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS1 | Savanna air-handling unit AHUS1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS1_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 843 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS1_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS1_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUS1_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS1 | Savanna air-handling unit AHUS1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS1_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 838 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS1_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS1_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUS1_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS1 | Savanna air-handling unit AHUS1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS1_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 840 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS1_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS1_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS1_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUS2_CCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS2 | Savanna air-handling unit AHUS2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS2_CCVlvCmd | CCVlvCmd | CCVlv Cmd; Cmd=Command; Vlv=Valve | Changes cooling capacity available to Savanna or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 831 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS2_CCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_CCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_CCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS2_CCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUS2_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS2 | Savanna air-handling unit AHUS2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS2_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to Savanna or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 815 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS2_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS2_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS2_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS2 | Savanna air-handling unit AHUS2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS2_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 830 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS2_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS2_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS2_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS2 | Savanna air-handling unit AHUS2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS2_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 829 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS2_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS2_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS2_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS2 | Savanna air-handling unit AHUS2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS2_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 828 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS2_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS2_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Heating valve command | u_AHUS2_HCVlvCmd | Heating valve command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS2 | Savanna air-handling unit AHUS2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS2_HCVlvCmd | HCVlvCmd | HotwaterControlVlvCommand | Changes heating capacity available to Savanna or to the shared hot-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 825 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS2_HCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_HCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_HCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS2_HCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Heating valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUS2_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS2 | Savanna air-handling unit AHUS2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS2_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting Savanna; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 820 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS2_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 4226 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS2_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUS2_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS2 | Savanna air-handling unit AHUS2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS2_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 817 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS2_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 3566 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS2_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUS2_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS2 | Savanna air-handling unit AHUS2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS2_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 824 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS2_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS2_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUS2_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS2 | Savanna air-handling unit AHUS2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS2_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 822 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS2_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS2_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUS2_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS2 | Savanna air-handling unit AHUS2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS2_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 818 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS2_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS2_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUS2_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS2 | Savanna air-handling unit AHUS2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS2_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 823 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS2_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS2_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS2_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUS3_CCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS3 | Savanna air-handling unit AHUS3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS3_CCVlvCmd | CCVlvCmd | CCVlv Cmd; Cmd=Command; Vlv=Valve | Changes cooling capacity available to Savanna or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 814 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS3_CCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_CCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_CCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS3_CCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUS3_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS3 | Savanna air-handling unit AHUS3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS3_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to Savanna or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 798 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS3_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS3_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS3_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS3 | Savanna air-handling unit AHUS3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS3_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 813 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS3_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS3_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS3_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS3 | Savanna air-handling unit AHUS3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS3_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 812 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS3_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS3_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS3_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS3 | Savanna air-handling unit AHUS3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS3_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 810 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS3_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS3_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Heating valve command | u_AHUS3_HCVlvCmd | Heating valve command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS3 | Savanna air-handling unit AHUS3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS3_HCVlvCmd | HCVlvCmd | HotwaterControlVlvCommand | Changes heating capacity available to Savanna or to the shared hot-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 809 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS3_HCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_HCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_HCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS3_HCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Heating valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUS3_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS3 | Savanna air-handling unit AHUS3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS3_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting Savanna; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 805 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS3_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 3689 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS3_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUS3_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS3 | Savanna air-handling unit AHUS3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS3_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 800 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS3_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 3202 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS3_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUS3_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS3 | Savanna air-handling unit AHUS3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS3_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 806 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS3_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS3_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUS3_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS3 | Savanna air-handling unit AHUS3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS3_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 807 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS3_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS3_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUS3_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS3 | Savanna air-handling unit AHUS3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS3_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 803 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS3_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS3_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUS3_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS3 | Savanna air-handling unit AHUS3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS3_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 804 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS3_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS3_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS3_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUS4_CCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS4 | Savanna air-handling unit AHUS4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS4_CCVlvCmd | CCVlvCmd | CCVlv Cmd; Cmd=Command; Vlv=Valve | Changes cooling capacity available to Savanna or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 797 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS4_CCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_CCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_CCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS4_CCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUS4_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS4 | Savanna air-handling unit AHUS4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS4_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to Savanna or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 782 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS4_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS4_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS4_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS4 | Savanna air-handling unit AHUS4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS4_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 796 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS4_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS4_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS4_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS4 | Savanna air-handling unit AHUS4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS4_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 795 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS4_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS4_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS4_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS4 | Savanna air-handling unit AHUS4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS4_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 794 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS4_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS4_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Heating valve command | u_AHUS4_HCVlvCmd | Heating valve command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS4 | Savanna air-handling unit AHUS4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS4_HCVlvCmd | HCVlvCmd | HotwaterControlVlvCommand | Changes heating capacity available to Savanna or to the shared hot-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 791 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS4_HCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_HCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_HCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS4_HCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Heating valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUS4_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS4 | Savanna air-handling unit AHUS4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS4_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting Savanna; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 787 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS4_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-04-27 | 3118 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS4_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUS4_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS4 | Savanna air-handling unit AHUS4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS4_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 784 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS4_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-04-27 | 2697 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS4_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUS4_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS4 | Savanna air-handling unit AHUS4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS4_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 790 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS4_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS4_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUS4_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS4 | Savanna air-handling unit AHUS4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS4_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 789 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS4_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS4_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUS4_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS4 | Savanna air-handling unit AHUS4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS4_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 785 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS4_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS4_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUS4_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS4 | Savanna air-handling unit AHUS4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS4_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 788 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS4_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS4_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS4_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUS5_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS5 | Savanna air-handling unit AHUS5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS5_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to Savanna or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 766 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS5_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS5_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS5_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS5 | Savanna air-handling unit AHUS5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS5_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 779 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS5_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS5_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS5_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS5 | Savanna air-handling unit AHUS5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS5_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 780 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS5_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS5_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS5_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS5 | Savanna air-handling unit AHUS5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS5_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 778 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS5_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS5_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUS5_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS5 | Savanna air-handling unit AHUS5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS5_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting Savanna; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 772 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS5_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 4242 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS5_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUS5_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS5 | Savanna air-handling unit AHUS5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS5_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 768 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS5_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 3645 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS5_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUS5_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS5 | Savanna air-handling unit AHUS5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS5_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 775 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS5_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS5_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUS5_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS5 | Savanna air-handling unit AHUS5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS5_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 774 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS5_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS5_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUS5_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS5 | Savanna air-handling unit AHUS5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS5_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 769 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS5_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS5_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUS5_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS5 | Savanna air-handling unit AHUS5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS5_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 773 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS5_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS5_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS5_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUS6_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS6 | Savanna air-handling unit AHUS6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS6_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to Savanna or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 751 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS6_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS6_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS6_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS6 | Savanna air-handling unit AHUS6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS6_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 765 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS6_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS6_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS6_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS6 | Savanna air-handling unit AHUS6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS6_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 764 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS6_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS6_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS6_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS6 | Savanna air-handling unit AHUS6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS6_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 762 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS6_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS6_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUS6_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS6 | Savanna air-handling unit AHUS6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS6_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting Savanna; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 758 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS6_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 3142 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS6_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUS6_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS6 | Savanna air-handling unit AHUS6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS6_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 754 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS6_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 2688 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS6_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUS6_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS6 | Savanna air-handling unit AHUS6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS6_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 759 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS6_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS6_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUS6_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS6 | Savanna air-handling unit AHUS6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS6_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 760 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS6_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS6_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUS6_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS6 | Savanna air-handling unit AHUS6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS6_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 755 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS6_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS6_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUS6_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS6 | Savanna air-handling unit AHUS6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS6_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 757 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS6_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS6_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS6_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUS7_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS7 | Savanna air-handling unit AHUS7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS7_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to Savanna or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 736 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS7_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS7_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS7_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS7 | Savanna air-handling unit AHUS7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS7_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 749 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS7_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS7_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS7_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS7 | Savanna air-handling unit AHUS7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS7_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 750 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS7_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS7_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUS7_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS7 | Savanna air-handling unit AHUS7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS7_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 748 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS7_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS7_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUS7_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS7 | Savanna air-handling unit AHUS7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS7_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting Savanna; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 743 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS7_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-04-01 | 2545 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS7_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUS7_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS7 | Savanna air-handling unit AHUS7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS7_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for Savanna. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 738 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS7_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-04-01 | 2183 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS7_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUS7_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS7 | Savanna air-handling unit AHUS7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS7_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 745 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS7_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS7_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUS7_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS7 | Savanna air-handling unit AHUS7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS7_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 744 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS7_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS7_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUS7_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS7 | Savanna air-handling unit AHUS7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS7_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Savanna. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 741 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS7_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS7_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUS7_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | AHUS7 | Savanna air-handling unit AHUS7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUS7_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 742 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUS7_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUS7_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUS7_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Solenoid valve / unknown valve | u_MiscSAV1_SV20 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV20 | SV20 | SV20 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 521 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV20 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 1409 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV20 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV20 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV20 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV21 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV21 | SV21 | SV21 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 520 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV21 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 2518 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV21 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV21 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV21 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV22 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV22 | SV22 | SV22 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 519 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV22 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 2527 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV22 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV22 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV22 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV23 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV23 | SV23 | SV23 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 517 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV23 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 2537 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV23 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV23 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV23 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV27 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV27 | SV27 | SV27 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 518 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV27 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 105 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV27 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV27 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV27 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV36 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV36 | SV36 | SV36 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 515 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV36 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 132 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV36 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV36 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV36 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV37 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV37 | SV37 | SV37 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 516 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV37 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 133 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV37 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV37 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV37 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV38 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV38 | SV38 | SV38 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 514 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV38 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 4935 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV38 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV38 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV38 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV39 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV39 | SV39 | SV39 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 513 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV39 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 4927 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV39 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV39 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV39 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV40 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV40 | SV40 | SV40 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 511 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV40 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 3409 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV40 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV40 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV40 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV41 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV41 | SV41 | SV41 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 512 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV41 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 5557 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV41 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV41 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV41 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV42 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV42 | SV42 | SV42 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 510 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV42 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 4395 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV42 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV42 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV42 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV43 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV43 | SV43 | SV43 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 509 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV43 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 129 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV43 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV43 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV43 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV45 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV45 | SV45 | SV45 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 507 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV45 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 4538 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV45 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV45 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV45 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV46 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV46 | SV46 | SV46 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 508 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV46 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 4474 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV46 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV46 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV46 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV47 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV47 | SV47 | SV47 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 506 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV47 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 4642 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV47 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV47 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV47 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV48 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV48 | SV48 | SV48 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 505 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV48 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 4600 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV48 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV48 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV48 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV49 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV49 | SV49 | SV49 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 504 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV49 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 2565 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV49 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV49 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV49 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV50 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV50 | SV50 | SV50 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 503 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV50 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 116 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV50 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV50 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV50 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV51 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV51 | SV51 | SV51 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 501 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV51 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 205 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV51 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV51 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV51 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV52 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV52 | SV52 | SV52 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 502 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV52 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 204 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV52 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV52 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV52 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV53 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV53 | SV53 | SV53 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 499 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV53 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 204 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV53 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV53 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV53 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV54 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV54 | SV54 | SV54 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 500 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV54 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 204 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV54 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV54 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV54 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV55 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV55 | SV55 | SV55 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 497 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV55 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 205 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV55 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV55 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV55 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV56 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV56 | SV56 | SV56 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 498 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV56 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 198 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV56 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV56 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV56 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV69 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV69 | SV69 | SV69 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 495 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV69 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 217 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV69 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV69 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV69 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV70 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV70 | SV70 | SV70 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 496 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV70 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 213 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV70 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV70 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV70 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscSAV1_SV8 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Savanna | Inventory BIOM=4, BIOMNAME=Savanna. | MiscSAV1 | Savanna miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscSAV1_SV8 | SV8 | SV8 | Changes hydronic/air/water flow through equipment serving Savanna. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 494 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCSAV1_SV8 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 238 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV8 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCSAV1_SV8 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCSAV1_SV8 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Cooling valve command | u_AHUD1_CCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD1 | Desert air-handling unit AHUD1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD1_CCVlvCmd | CCVlvCmd | CCVlv Cmd; Cmd=Command; Vlv=Valve | Changes cooling capacity available to Desert or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1170 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD1_CCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_CCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_CCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD1_CCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUD1_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD1 | Desert air-handling unit AHUD1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD1_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to Desert or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1150 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD1_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD1_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUD1_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD1 | Desert air-handling unit AHUD1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD1_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for Desert. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1168 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD1_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD1_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUD1_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD1 | Desert air-handling unit AHUD1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD1_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for Desert. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1169 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD1_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD1_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUD1_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD1 | Desert air-handling unit AHUD1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD1_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for Desert. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1167 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD1_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD1_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Heating valve command | u_AHUD1_HCVlvCmd | Heating valve command | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD1 | Desert air-handling unit AHUD1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD1_HCVlvCmd | HCVlvCmd | HotwaterControlVlvCommand | Changes heating capacity available to Desert or to the shared hot-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1163 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD1_HCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_HCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_HCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD1_HCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Heating valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUD1_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD1 | Desert air-handling unit AHUD1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD1_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting Desert; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1159 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD1_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 2703 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD1_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUD1_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD1 | Desert air-handling unit AHUD1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD1_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for Desert. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1152 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD1_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 2323 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD1_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUD1_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD1 | Desert air-handling unit AHUD1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD1_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Desert. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1162 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD1_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD1_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUD1_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD1 | Desert air-handling unit AHUD1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD1_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving Desert. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1160 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD1_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD1_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUD1_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD1 | Desert air-handling unit AHUD1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD1_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Desert. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1154 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD1_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD1_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUD1_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD1 | Desert air-handling unit AHUD1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD1_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Desert. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1161 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD1_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD1_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD1_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUD2_CCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD2 | Desert air-handling unit AHUD2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD2_CCVlvCmd | CCVlvCmd | CCVlv Cmd; Cmd=Command; Vlv=Valve | Changes cooling capacity available to Desert or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1149 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD2_CCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_CCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_CCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD2_CCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUD2_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD2 | Desert air-handling unit AHUD2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD2_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to Desert or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1130 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD2_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD2_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUD2_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD2 | Desert air-handling unit AHUD2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD2_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for Desert. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1147 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD2_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD2_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUD2_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD2 | Desert air-handling unit AHUD2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD2_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for Desert. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1148 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD2_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD2_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUD2_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD2 | Desert air-handling unit AHUD2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD2_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for Desert. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1146 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD2_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD2_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Heating valve command | u_AHUD2_HCVlvCmd | Heating valve command | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD2 | Desert air-handling unit AHUD2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD2_HCVlvCmd | HCVlvCmd | HotwaterControlVlvCommand | Changes heating capacity available to Desert or to the shared hot-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1141 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD2_HCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_HCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_HCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD2_HCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Heating valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUD2_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD2 | Desert air-handling unit AHUD2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD2_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting Desert; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1137 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD2_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 3997 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD2_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUD2_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD2 | Desert air-handling unit AHUD2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD2_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for Desert. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1131 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD2_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 3513 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD2_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUD2_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD2 | Desert air-handling unit AHUD2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD2_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Desert. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1142 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD2_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD2_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUD2_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD2 | Desert air-handling unit AHUD2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD2_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving Desert. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1140 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD2_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD2_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUD2_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD2 | Desert air-handling unit AHUD2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD2_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Desert. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1134 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD2_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD2_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUD2_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD2 | Desert air-handling unit AHUD2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD2_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Desert. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1139 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD2_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD2_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD2_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUD3_CCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD3 | Desert air-handling unit AHUD3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD3_CCVlvCmd | CCVlvCmd | CCVlv Cmd; Cmd=Command; Vlv=Valve | Changes cooling capacity available to Desert or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1127 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD3_CCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_CCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_CCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD3_CCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUD3_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD3 | Desert air-handling unit AHUD3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD3_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to Desert or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1108 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD3_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD3_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUD3_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD3 | Desert air-handling unit AHUD3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD3_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for Desert. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1128 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD3_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD3_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUD3_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD3 | Desert air-handling unit AHUD3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD3_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for Desert. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1125 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD3_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD3_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUD3_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD3 | Desert air-handling unit AHUD3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD3_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for Desert. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1126 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD3_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD3_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Heating valve command | u_AHUD3_HCVlvCmd | Heating valve command | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD3 | Desert air-handling unit AHUD3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD3_HCVlvCmd | HCVlvCmd | HotwaterControlVlvCommand | Changes heating capacity available to Desert or to the shared hot-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1121 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD3_HCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_HCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_HCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD3_HCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Heating valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUD3_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD3 | Desert air-handling unit AHUD3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD3_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting Desert; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1117 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD3_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | present | 3825 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD3_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUD3_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD3 | Desert air-handling unit AHUD3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD3_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for Desert. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1109 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD3_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | present | 3459 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD3_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUD3_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD3 | Desert air-handling unit AHUD3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD3_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Desert. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1120 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD3_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD3_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUD3_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD3 | Desert air-handling unit AHUD3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD3_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving Desert. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1118 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD3_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD3_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUD3_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD3 | Desert air-handling unit AHUD3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD3_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving Desert. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1112 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD3_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD3_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUD3_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Desert | Inventory BIOM=5, BIOMNAME=Desert. | AHUD3 | Desert air-handling unit AHUD3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUD3_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Desert. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1119 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUD3_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUD3_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUD3_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Damper control | u_MiscDES1_DprCloseSp | Damper control | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_DprCloseSp | DprCloseSp | Dpr Close Sp | Changes ventilation path, outside-air fraction, or air exchange for Desert. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 687 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_DPRCLOSESP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_DPRCLOSESP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_DPRCLOSESP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_DPRCLOSESP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Damper control | u_MiscDES1_DprOpenSp | Damper control | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_DprOpenSp | DprOpenSp | DamperOpenSetpoint | Changes ventilation path, outside-air fraction, or air exchange for Desert. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 685 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_DPROPENSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_DPROPENSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_DPROPENSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_DPROPENSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Damper control | u_MiscDES1_RoofDmpCmd | Damper control | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_RoofDmpCmd | RoofDmpCmd | Roof Dmp Cmd; Cmd=Command; Dmp=Damper | Changes ventilation path, outside-air fraction, or air exchange for Desert. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 666 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_ROOFDMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | present | 2143 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_ROOFDMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_ROOFDMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_ROOFDMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Damper control.
Pump command | u_MiscDES1_WTP3PmpCmd | Pump command | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_WTP3PmpCmd | WTP3PmpCmd | 'WTP3' Pump Command (South Lung reservoir) | Changes water-loop circulation or pressure serving Desert or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 643 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_WTP3PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 4174 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_WTP3PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_WTP3PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_WTP3PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command.
Rain / irrigation control | u_MiscDES1_MainRainFlwRat | Rain / irrigation control | needs engineering verification | Low - equipment meaning requires engineering verification | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_MainRainFlwRat | MainRainFlwRat | Main Rain Flw Rat; FlwRat=FlowRate; Flw=Flow | Changes water input or irrigation forcing for Desert. | Source-term control parameter | Use as prescribed water-input/source forcing or as a candidate manipulated variable in control/inversion. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 675 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_MAINRAINFLWRAT | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | L/min | m^3/s | Q = VALUE * 1e-3 / 60 | SENSOR | units=u:liters per minute;L/min;(m3)(s-1);*1.6666666666666667E-5; | Flow rate | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_MAINRAINFLWRAT live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE * 1e-3 / 60 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_MAINRAINFLWRAT t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_MAINRAINFLWRAT | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Rain / irrigation control. Low - equipment meaning requires engineering verification
Rain / irrigation control | u_MiscDES1_MaxRainTnkLvlSp | Rain / irrigation control | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_MaxRainTnkLvlSp | MaxRainTnkLvlSp | Max Rain Tnk Lvl Sp; Lvl=Level; Tnk=Tank | Changes water input or irrigation forcing for Desert. | Source-term control parameter | Use as prescribed water-input/source forcing or as a candidate manipulated variable in control/inversion. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 674 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_MAXRAINTNKLVLSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | inH2O | m water | h_m = VALUE * 0.0254 | SENSOR | units=u:inches of water;in/wc;(m-1)(kg)(s-2);*248.84; | Water level | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_MAXRAINTNKLVLSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE * 0.0254 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_MAXRAINTNKLVLSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_MAXRAINTNKLVLSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Rain / irrigation control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Rain / irrigation control | u_MiscDES1_MinRainTnkLvlSp | Rain / irrigation control | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_MinRainTnkLvlSp | MinRainTnkLvlSp | Min Rain Tnk Lvl Sp; Lvl=Level; Min=Minimum; Tnk=Tank | Changes water input or irrigation forcing for Desert. | Source-term control parameter | Use as prescribed water-input/source forcing or as a candidate manipulated variable in control/inversion. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 672 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_MINRAINTNKLVLSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | inH2O | m water | h_m = VALUE * 0.0254 | SENSOR | units=u:inches of water;in/wc;(m-1)(kg)(s-2);*248.84; | Water level | 2022-01-22 | present | 149090 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_MINRAINTNKLVLSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE * 0.0254 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_MINRAINTNKLVLSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_MINRAINTNKLVLSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Rain / irrigation control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Rain / irrigation control | u_MiscDES1_RainPmpPsrSp | Rain / irrigation control | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_RainPmpPsrSp | RainPmpPsrSp | Rain Pmp Psr Sp; Pmp=Pump; Psr=Pressure | Changes water input or irrigation forcing for Desert. | Source-term control parameter | Use as prescribed water-input/source forcing or as a candidate manipulated variable in control/inversion. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 668 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_RAINPMPPSRSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | psi | Pa | p_Pa = VALUE * 6894.757 | SENSOR | units=u:pounds per square inch;psi;(m-1)(kg)(s-2);*6894.75729; | Pressure | 2022-01-22 | present | 149090 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_RAINPMPPSRSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE * 6894.757 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_RAINPMPPSRSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_RAINPMPPSRSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Rain / irrigation control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Rain / irrigation control | u_MiscDES1_RainVlv4Cmd | Rain / irrigation control | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_RainVlv4Cmd | RainVlv4Cmd | Rain Vlv4Cmd; Cmd=Command; Vlv=Valve | Changes water input or irrigation forcing for Desert. | Source-term control parameter | Use as prescribed water-input/source forcing or as a candidate manipulated variable in control/inversion. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 669 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_RAINVLV4CMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | VALVE COMMAND | trueText=s:OPEN¦falseText=s:CLOSED¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | present | 8758 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_RAINVLV4CMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_RAINVLV4CMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_RAINVLV4CMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Rain / irrigation control.
Solenoid valve / unknown valve | u_MiscDES1_SV04 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_SV04 | SV04 | SV04 | Changes hydronic/air/water flow through equipment serving Desert. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 657 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_SV04 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 214 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV04 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV04 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_SV04 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscDES1_SV05 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_SV05 | SV05 | SV05 | Changes hydronic/air/water flow through equipment serving Desert. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 656 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_SV05 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 220 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV05 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV05 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_SV05 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscDES1_SV08 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_SV08 | SV08 | SV08 | Changes hydronic/air/water flow through equipment serving Desert. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 654 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_SV08 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 217 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV08 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV08 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_SV08 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscDES1_SV09 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_SV09 | SV09 | SV09 | Changes hydronic/air/water flow through equipment serving Desert. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 655 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_SV09 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 219 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV09 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV09 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_SV09 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscDES1_SV31 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_SV31 | SV31 | SV31 | Changes hydronic/air/water flow through equipment serving Desert. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 652 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_SV31 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 1917 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV31 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV31 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_SV31 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscDES1_SV33 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_SV33 | SV33 | SV33 | Changes hydronic/air/water flow through equipment serving Desert. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 653 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_SV33 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 2160 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV33 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV33 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_SV33 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscDES1_SV34 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_SV34 | SV34 | SV34 | Changes hydronic/air/water flow through equipment serving Desert. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 651 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_SV34 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 2357 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV34 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV34 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_SV34 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscDES1_SV35 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_SV35 | SV35 | SV35 | Changes hydronic/air/water flow through equipment serving Desert. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 650 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_SV35 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 2246 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV35 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV35 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_SV35 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscDES1_SV60 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_SV60 | SV60 | SV60 | Changes hydronic/air/water flow through equipment serving Desert. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 648 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_SV60 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 204 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV60 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV60 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_SV60 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscDES1_SV71 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_SV71 | SV71 | SV71 | Changes hydronic/air/water flow through equipment serving Desert. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 649 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_SV71 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 921 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV71 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV71 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_SV71 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscDES1_SV80 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_SV80 | SV80 | SV80 | Changes hydronic/air/water flow through equipment serving Desert. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 647 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_SV80 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 2318 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV80 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV80 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_SV80 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Solenoid valve / unknown valve | u_MiscDES1_SV81 | Solenoid valve / unknown valve | binary valve command or status/command point | Low - equipment meaning requires engineering verification | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES1 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_SV81 | SV81 | SV81 | Changes hydronic/air/water flow through equipment serving Desert. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 646 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_SV81 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 2151 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV81 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SV81 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_SV81 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Solenoid valve / unknown valve. Low - equipment meaning requires engineering verification
Rain / irrigation control | u_MiscDES2_RainPmpCmd22 | Rain / irrigation control | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES2 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES2_RainPmpCmd22 | RainPmpCmd22 | Rain Pmp Cmd22; Cmd=Command; Pmp=Pump | Changes water input or irrigation forcing for Desert. | Source-term control parameter | Use as prescribed water-input/source forcing or as a candidate manipulated variable in control/inversion. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 632 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES2_RAINPMPCMD22 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-26 | 2204 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES2_RAINPMPCMD22 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES2_RAINPMPCMD22 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES2_RAINPMPCMD22 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Rain / irrigation control.
Rain / irrigation control | u_MiscDES2_RainPmpEnable | Rain / irrigation control | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES2 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES2_RainPmpEnable | RainPmpEnable | Rain Pmp Enable; Pmp=Pump | Changes water input or irrigation forcing for Desert. | Source-term control parameter | Use as prescribed water-input/source forcing or as a candidate manipulated variable in control/inversion. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 633 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES2_RAINPMPENABLE | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 291 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES2_RAINPMPENABLE live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES2_RAINPMPENABLE t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES2_RAINPMPENABLE | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Rain / irrigation control.
Rain / irrigation control | u_MiscDES2_RainPmpPsrSpt | Rain / irrigation control | setpoint | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MiscDES2 | Desert miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES2_RainPmpPsrSpt | RainPmpPsrSpt | Rain Pmp Psr Spt; Pmp=Pump; Psr=Pressure | Changes water input or irrigation forcing for Desert. | Source-term control parameter | Use as prescribed water-input/source forcing or as a candidate manipulated variable in control/inversion. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 630 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES2_RAINPMPPSRSPT | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | psi | Pa | p_Pa = VALUE * 6894.757 | SENSOR | units=u:pounds per square inch;psi;(m-1)(kg)(s-2);*6894.75729;¦precision=i:1 | Pressure | 2022-01-22 | present | 149090 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES2_RAINPMPPSRSPT live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE * 6894.757 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES2_RAINPMPPSRSPT t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES2_RAINPMPPSRSPT | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Rain / irrigation control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Rain / irrigation control | u_MischDES2_RainPmpCmd23 | Rain / irrigation control | command | High - name is command/setpoint for named climate equipment | Desert | Inventory BIOM=5, BIOMNAME=Desert. | MischDES2 | Desert equipment tag MischDES2; use BMS path for physical lookup. | /UAB2_BIO1/B4000_MischDES2_RainPmpCmd23 | RainPmpCmd23 | Rain Pmp Cmd23; Cmd=Command; Pmp=Pump | Changes water input or irrigation forcing for Desert. | Source-term control parameter | Use as prescribed water-input/source forcing or as a candidate manipulated variable in control/inversion. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 484 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCHDES2_RAINPMPCMD23 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-08 | 2026-05-01 | 19601 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCHDES2_RAINPMPCMD23 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCHDES2_RAINPMPCMD23 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCHDES2_RAINPMPCMD23 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Rain / irrigation control.
Cooling valve command | u_AHUL1_CCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL1 | LEO air-handling unit AHUL1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL1_CCVlvCmd | CCVlvCmd | CCVlv Cmd; Cmd=Command; Vlv=Valve | Changes cooling capacity available to LEO or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1107 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL1_CCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_CCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_CCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL1_CCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUL1_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL1 | LEO air-handling unit AHUL1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL1_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to LEO or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1087 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL1_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL1_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL1_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL1 | LEO air-handling unit AHUL1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL1_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1104 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL1_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL1_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL1_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL1 | LEO air-handling unit AHUL1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL1_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1103 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL1_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL1_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL1_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL1 | LEO air-handling unit AHUL1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL1_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1101 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL1_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL1_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Heating valve command | u_AHUL1_HCVlvCmd | Heating valve command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL1 | LEO air-handling unit AHUL1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL1_HCVlvCmd | HCVlvCmd | HotwaterControlVlvCommand | Changes heating capacity available to LEO or to the shared hot-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1099 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL1_HCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_HCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_HCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL1_HCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Heating valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUL1_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL1 | LEO air-handling unit AHUL1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL1_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting LEO; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1094 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL1_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 727 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL1_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUL1_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL1 | LEO air-handling unit AHUL1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL1_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1090 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL1_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 359 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL1_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUL1_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL1 | LEO air-handling unit AHUL1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL1_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1098 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL1_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL1_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL1_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL1 | LEO air-handling unit AHUL1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL1_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1096 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL1_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL1_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL1_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL1 | LEO air-handling unit AHUL1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL1_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1092 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL1_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL1_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUL1_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL1 | LEO air-handling unit AHUL1; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL1_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving LEO. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1095 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL1_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL1_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL1_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUL2_CCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL2 | LEO air-handling unit AHUL2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL2_CCVlvCmd | CCVlvCmd | CCVlv Cmd; Cmd=Command; Vlv=Valve | Changes cooling capacity available to LEO or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1085 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL2_CCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_CCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_CCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL2_CCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUL2_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL2 | LEO air-handling unit AHUL2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL2_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to LEO or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1068 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL2_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL2_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL2_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL2 | LEO air-handling unit AHUL2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL2_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1084 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL2_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL2_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL2_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL2 | LEO air-handling unit AHUL2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL2_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1082 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL2_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL2_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL2_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL2 | LEO air-handling unit AHUL2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL2_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1083 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL2_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL2_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Heating valve command | u_AHUL2_HCVlvCmd | Heating valve command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL2 | LEO air-handling unit AHUL2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL2_HCVlvCmd | HCVlvCmd | HotwaterControlVlvCommand | Changes heating capacity available to LEO or to the shared hot-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1078 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL2_HCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_HCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_HCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL2_HCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Heating valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUL2_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL2 | LEO air-handling unit AHUL2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL2_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting LEO; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1075 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL2_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 787 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL2_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUL2_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL2 | LEO air-handling unit AHUL2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL2_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1070 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL2_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 464 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL2_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUL2_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL2 | LEO air-handling unit AHUL2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL2_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1076 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL2_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL2_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL2_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL2 | LEO air-handling unit AHUL2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL2_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1077 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL2_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL2_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL2_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL2 | LEO air-handling unit AHUL2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL2_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1073 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL2_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL2_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUL2_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL2 | LEO air-handling unit AHUL2; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL2_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving LEO. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1074 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL2_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL2_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL2_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUL3_CCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL3 | LEO air-handling unit AHUL3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL3_CCVlvCmd | CCVlvCmd | CCVlv Cmd; Cmd=Command; Vlv=Valve | Changes cooling capacity available to LEO or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1065 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL3_CCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_CCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_CCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL3_CCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUL3_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL3 | LEO air-handling unit AHUL3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL3_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to LEO or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1044 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL3_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL3_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL3_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL3 | LEO air-handling unit AHUL3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL3_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1062 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL3_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | 2023-02-16 | 37414 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL3_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL3_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL3 | LEO air-handling unit AHUL3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL3_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1061 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL3_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | 2022-05-04 | 9809 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL3_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL3_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL3 | LEO air-handling unit AHUL3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL3_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1060 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL3_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | 2023-02-16 | 37414 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL3_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Heating valve command | u_AHUL3_HCVlvCmd | Heating valve command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL3 | LEO air-handling unit AHUL3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL3_HCVlvCmd | HCVlvCmd | HotwaterControlVlvCommand | Changes heating capacity available to LEO or to the shared hot-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1057 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL3_HCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_HCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_HCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL3_HCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Heating valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUL3_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL3 | LEO air-handling unit AHUL3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL3_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting LEO; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1052 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL3_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 2297 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL3_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUL3_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL3 | LEO air-handling unit AHUL3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL3_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1048 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL3_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 1955 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL3_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUL3_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL3 | LEO air-handling unit AHUL3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL3_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1055 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL3_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL3_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL3_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL3 | LEO air-handling unit AHUL3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL3_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1054 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL3_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL3_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL3_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL3 | LEO air-handling unit AHUL3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL3_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1050 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL3_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL3_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL3_SATmpSp1 | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL3 | LEO air-handling unit AHUL3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL3_SATmpSp1 | SATmpSp1 | SATmp Sp1; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Tmp=Temperature | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1049 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL3_SATMPSP1 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | 2022-05-18 | 11156 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_SATMPSP1 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_SATMPSP1 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL3_SATMPSP1 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUL3_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL3 | LEO air-handling unit AHUL3; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL3_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving LEO. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1053 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL3_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL3_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL3_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUL4_CCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL4 | LEO air-handling unit AHUL4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL4_CCVlvCmd | CCVlvCmd | CCVlv Cmd; Cmd=Command; Vlv=Valve | Changes cooling capacity available to LEO or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1043 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL4_CCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_CCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_CCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL4_CCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUL4_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL4 | LEO air-handling unit AHUL4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL4_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to LEO or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1022 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL4_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL4_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL4_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL4 | LEO air-handling unit AHUL4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL4_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1038 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL4_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL4_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL4_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL4 | LEO air-handling unit AHUL4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL4_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1039 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL4_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL4_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL4_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL4 | LEO air-handling unit AHUL4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL4_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1037 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL4_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL4_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Heating valve command | u_AHUL4_HCVlvCmd | Heating valve command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL4 | LEO air-handling unit AHUL4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL4_HCVlvCmd | HCVlvCmd | HotwaterControlVlvCommand | Changes heating capacity available to LEO or to the shared hot-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1033 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL4_HCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_HCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_HCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL4_HCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Heating valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUL4_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL4 | LEO air-handling unit AHUL4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL4_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting LEO; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1029 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL4_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 824 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL4_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUL4_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL4 | LEO air-handling unit AHUL4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL4_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1024 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL4_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 475 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL4_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUL4_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL4 | LEO air-handling unit AHUL4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL4_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1031 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL4_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL4_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL4_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL4 | LEO air-handling unit AHUL4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL4_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1032 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL4_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL4_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL4_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL4 | LEO air-handling unit AHUL4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL4_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1028 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL4_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL4_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL4_SATmpSp1 | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL4 | LEO air-handling unit AHUL4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL4_SATmpSp1 | SATmpSp1 | SATmp Sp1; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Tmp=Temperature | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1025 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL4_SATMPSP1 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_SATMPSP1 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_SATMPSP1 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL4_SATMPSP1 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUL4_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL4 | LEO air-handling unit AHUL4; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL4_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving LEO. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1030 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL4_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL4_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL4_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUL5_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL5 | LEO air-handling unit AHUL5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL5_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to LEO or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1005 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL5_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL5_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL5_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL5 | LEO air-handling unit AHUL5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL5_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1019 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL5_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL5_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL5_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL5 | LEO air-handling unit AHUL5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL5_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1018 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL5_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL5_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL5_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL5 | LEO air-handling unit AHUL5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL5_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1016 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL5_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL5_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUL5_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL5 | LEO air-handling unit AHUL5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL5_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting LEO; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1011 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL5_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 2949 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL5_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUL5_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL5 | LEO air-handling unit AHUL5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL5_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1008 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL5_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 2563 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL5_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUL5_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL5 | LEO air-handling unit AHUL5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL5_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1014 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL5_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL5_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL5_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL5 | LEO air-handling unit AHUL5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL5_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1013 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL5_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL5_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL5_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL5 | LEO air-handling unit AHUL5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL5_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1009 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL5_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL5_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUL5_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL5 | LEO air-handling unit AHUL5; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL5_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving LEO. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1012 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL5_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL5_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL5_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUL6_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL6 | LEO air-handling unit AHUL6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL6_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to LEO or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 990 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL6_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL6_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL6_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL6 | LEO air-handling unit AHUL6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL6_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1004 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL6_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL6_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL6_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL6 | LEO air-handling unit AHUL6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL6_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1003 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL6_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL6_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL6_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL6 | LEO air-handling unit AHUL6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL6_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1001 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL6_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL6_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUL6_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL6 | LEO air-handling unit AHUL6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL6_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting LEO; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 996 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL6_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 2693 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL6_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUL6_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL6 | LEO air-handling unit AHUL6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL6_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 992 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL6_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 2373 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL6_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUL6_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL6 | LEO air-handling unit AHUL6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL6_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 1000 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL6_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL6_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL6_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL6 | LEO air-handling unit AHUL6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL6_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 998 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL6_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL6_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL6_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL6 | LEO air-handling unit AHUL6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL6_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 994 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL6_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL6_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUL6_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL6 | LEO air-handling unit AHUL6; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL6_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving LEO. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 997 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL6_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL6_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL6_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUL7_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL7 | LEO air-handling unit AHUL7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL7_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to LEO or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 975 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL7_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL7_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL7_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL7 | LEO air-handling unit AHUL7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL7_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 989 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL7_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL7_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL7_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL7 | LEO air-handling unit AHUL7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL7_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 988 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL7_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL7_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL7_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL7 | LEO air-handling unit AHUL7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL7_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 986 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL7_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL7_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUL7_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL7 | LEO air-handling unit AHUL7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL7_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting LEO; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 981 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL7_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 3604 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL7_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUL7_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL7 | LEO air-handling unit AHUL7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL7_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 977 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL7_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 3276 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL7_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUL7_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL7 | LEO air-handling unit AHUL7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL7_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 985 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL7_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL7_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL7_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL7 | LEO air-handling unit AHUL7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL7_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 983 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL7_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL7_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL7_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL7 | LEO air-handling unit AHUL7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL7_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 979 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL7_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL7_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL7_SATmpSp1 | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL7 | LEO air-handling unit AHUL7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL7_SATmpSp1 | SATmpSp1 | SATmp Sp1; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Tmp=Temperature | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 978 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL7_SATMPSP1 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_SATMPSP1 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_SATMPSP1 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL7_SATMPSP1 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUL7_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL7 | LEO air-handling unit AHUL7; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL7_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving LEO. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 982 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL7_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL7_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL7_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUL8_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL8 | LEO air-handling unit AHUL8; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL8_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to LEO or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 958 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL8_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL8_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL8_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL8 | LEO air-handling unit AHUL8; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL8_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 973 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL8_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL8_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL8_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL8 | LEO air-handling unit AHUL8; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL8_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 972 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL8_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL8_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL8_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL8 | LEO air-handling unit AHUL8; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL8_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 971 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL8_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL8_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUL8_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL8 | LEO air-handling unit AHUL8; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL8_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting LEO; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 964 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL8_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 1985 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL8_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUL8_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL8 | LEO air-handling unit AHUL8; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL8_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 960 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL8_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 1767 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL8_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUL8_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL8 | LEO air-handling unit AHUL8; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL8_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 968 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL8_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL8_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL8_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL8 | LEO air-handling unit AHUL8; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL8_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 967 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL8_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL8_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL8_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL8 | LEO air-handling unit AHUL8; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL8_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 962 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL8_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL8_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL8_SATmpSp1 | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL8 | LEO air-handling unit AHUL8; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL8_SATmpSp1 | SATmpSp1 | SATmp Sp1; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Tmp=Temperature | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 963 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL8_SATMPSP1 | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_SATMPSP1 live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_SATMPSP1 t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL8_SATMPSP1 | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUL8_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL8 | LEO air-handling unit AHUL8; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL8_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving LEO. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 966 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL8_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL8_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL8_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Cooling valve command | u_AHUL9_TWCCVlvCmd | Cooling valve command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL9 | LEO air-handling unit AHUL9; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL9_TWCCVlvCmd | TWCCVlvCmd | ?Tower Water Condensor Control Valve Command (Chiller) | Changes cooling capacity available to LEO or to the shared chilled-water loop. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 944 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL9_TWCCVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_TWCCVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_TWCCVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL9_TWCCVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Cooling valve command. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL9_EDCmd | Economizer / damper control | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL9 | LEO air-handling unit AHUL9; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL9_EDCmd | EDCmd | EDCmd; Cmd=Command | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 957 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL9_EDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_EDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_EDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL9_EDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL9_EDPos | Economizer / damper control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL9 | LEO air-handling unit AHUL9; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL9_EDPos | EDPos | EDPos; Pos=Position | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 955 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL9_EDPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_EDPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_EDPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL9_EDPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Economizer / damper control | u_AHUL9_EDPosSp | Economizer / damper control | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL9 | LEO air-handling unit AHUL9; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL9_EDPosSp | EDPosSp | EconoDisc Position Setpoint | Changes ventilation path, outside-air fraction, or air exchange for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 956 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL9_EDPOSSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_EDPOSSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_EDPOSSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL9_EDPOSSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Economizer / damper control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Occupancy / schedule command | u_AHUL9_OccCmd | Occupancy / schedule command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL9 | LEO air-handling unit AHUL9; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL9_OccCmd | OccCmd | OccupancyCommand | Potential control input affecting LEO; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 949 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL9_OCCCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 1610 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_OCCCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_OCCCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL9_OCCCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Occupancy / schedule command.
Supply fan command | u_AHUL9_SFCmd | Supply fan command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL9 | LEO air-handling unit AHUL9; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL9_SFCmd | SFCmd | ?Fan Command | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 945 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL9_SFCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF |  | 2021-10-07 | 2026-05-01 | 1305 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_SFCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_SFCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL9_SFCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Supply fan command.
Temperature setpoint | u_AHUL9_MaxSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL9 | LEO air-handling unit AHUL9; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL9_MaxSATmpSp | MaxSATmpSp | ?Maximum Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 951 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL9_MAXSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_MAXSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_MAXSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL9_MAXSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL9_MinSATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL9 | LEO air-handling unit AHUL9; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL9_MinSATmpSp | MinSATmpSp | Min SATmp Sp; SATmpSp=?Supply Air Temperature Setpoint; SATmp=?Supply Air Temperature; Min=Minimum; Tmp=Temperature | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 952 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL9_MINSATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_MINSATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_MINSATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL9_MINSATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_AHUL9_SATmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL9 | LEO air-handling unit AHUL9; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL9_SATmpSp | SATmpSp | ?Supply Air Temperature Setpoint | Sets target temperature used by equipment serving LEO. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 948 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL9_SATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223;¦precision=i:1¦min=d:-inf¦max=d:+inf | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_SATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_SATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL9_SATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_AHUL9_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | AHUL9 | LEO air-handling unit AHUL9; use equipment tag and BMS path to find the physical AHU. | /UAB2_BIO1/B4000_AHUL9_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving LEO. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 950 | BIO2CONTROLS | UAB2_BIO1_B4000_AHUL9_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_AHUL9_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_AHUL9_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Fan / VFD speed control | u_MiscLEO1_EastExhFanCmd | Fan / VFD speed control | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | MiscLEO1 | LEO equipment tag MiscLEO1; use BMS path for physical lookup. | /UAB2_BIO1/B4000_MiscLEO1_EastExhFanCmd | EastExhFanCmd | East Exh Fan Cmd; Cmd=Command; Exh=Exhaust | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 605 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCLEO1_EASTEXHFANCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 164 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO1_EASTEXHFANCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO1_EASTEXHFANCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCLEO1_EASTEXHFANCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control.
Fan / VFD speed control | u_MiscLEO1_EastInjFanCmd | Fan / VFD speed control | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | MiscLEO1 | LEO equipment tag MiscLEO1; use BMS path for physical lookup. | /UAB2_BIO1/B4000_MiscLEO1_EastInjFanCmd | EastInjFanCmd | East Inj Fan Cmd; Cmd=Command; Inj=Injection | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 601 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCLEO1_EASTINJFANCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 208 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO1_EASTINJFANCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO1_EASTINJFANCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCLEO1_EASTINJFANCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control.
Fan / VFD speed control | u_MiscLEO1_EastInjFanSpd | Fan / VFD speed control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | MiscLEO1 | LEO equipment tag MiscLEO1; use BMS path for physical lookup. | /UAB2_BIO1/B4000_MiscLEO1_EastInjFanSpd | EastInjFanSpd | East Inj Fan Spd; Inj=Injection; Spd=Speed | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 599 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCLEO1_EASTINJFANSPD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; | Flow | 2022-01-22 | present | 149090 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO1_EASTINJFANSPD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO1_EASTINJFANSPD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCLEO1_EASTINJFANSPD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Fan / VFD speed control | u_MiscLEO1_WestExhFanCmd | Fan / VFD speed control | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | MiscLEO1 | LEO equipment tag MiscLEO1; use BMS path for physical lookup. | /UAB2_BIO1/B4000_MiscLEO1_WestExhFanCmd | WestExhFanCmd | West Exh Fan Cmd; Cmd=Command; Exh=Exhaust | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 584 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCLEO1_WESTEXHFANCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2024-04-06 | 67 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO1_WESTEXHFANCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO1_WESTEXHFANCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCLEO1_WESTEXHFANCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control.
Fan / VFD speed control | u_MiscLEO1_WestExhFanSpd | Fan / VFD speed control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | MiscLEO1 | LEO equipment tag MiscLEO1; use BMS path for physical lookup. | /UAB2_BIO1/B4000_MiscLEO1_WestExhFanSpd | WestExhFanSpd | West Exh Fan Spd; Exh=Exhaust; Spd=Speed | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 585 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCLEO1_WESTEXHFANSPD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | Level SENSOR (unit-less) | units=u:null;;;; | Fan speed | 2022-01-22 | 2024-04-09 | 77495 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO1_WESTEXHFANSPD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO1_WESTEXHFANSPD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCLEO1_WESTEXHFANSPD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Fan / VFD speed control | u_MiscLEO1_WestInjFanCmd | Fan / VFD speed control | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | MiscLEO1 | LEO equipment tag MiscLEO1; use BMS path for physical lookup. | /UAB2_BIO1/B4000_MiscLEO1_WestInjFanCmd | WestInjFanCmd | West Inj Fan Cmd; Cmd=Command; Inj=Injection | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 582 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCLEO1_WESTINJFANCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2024-04-06 | 73 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO1_WESTINJFANCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO1_WESTINJFANCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCLEO1_WESTINJFANCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control.
Fan / VFD speed control | u_MiscLEO1_WestInjFanSpd | Fan / VFD speed control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | MiscLEO1 | LEO equipment tag MiscLEO1; use BMS path for physical lookup. | /UAB2_BIO1/B4000_MiscLEO1_WestInjFanSpd | WestInjFanSpd | West Inj Fan Spd; Inj=Injection; Spd=Speed | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 581 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCLEO1_WESTINJFANSPD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; | Fan speed | 2022-01-22 | 2024-04-09 | 77495 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO1_WESTINJFANSPD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO1_WESTINJFANSPD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCLEO1_WESTINJFANSPD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Fan / VFD direction command | u_MiscLEO2_WestLowerFwdCmd | Fan / VFD direction command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | MiscLEO2 | LEO equipment tag MiscLEO2; use BMS path for physical lookup. | /UAB2_BIO1/B4000_MiscLEO2_WestLowerFwdCmd | WestLowerFwdCmd | West Lower Fwd Cmd; Cmd=Command | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 19404 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCLEO2_WESTLOWERFWDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE COMMAND | trueText=s:Run¦falseText=s:Stop¦range=E:bacnet:BacnetBinaryPv |  | 2024-04-10 | 2026-04-27 | 346 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO2_WESTLOWERFWDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO2_WESTLOWERFWDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCLEO2_WESTLOWERFWDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD direction command.
Fan / VFD direction command | u_MiscLEO2_WestLowerRevCmd | Fan / VFD direction command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | MiscLEO2 | LEO equipment tag MiscLEO2; use BMS path for physical lookup. | /UAB2_BIO1/B4000_MiscLEO2_WestLowerRevCmd | WestLowerRevCmd | West Lower Rev Cmd; Cmd=Command | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 19403 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCLEO2_WESTLOWERREVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE COMMAND | trueText=s:Run¦falseText=s:Stop¦range=E:bacnet:BacnetBinaryPv |  | 2024-04-10 | 2026-04-27 | 149 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO2_WESTLOWERREVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO2_WESTLOWERREVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCLEO2_WESTLOWERREVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD direction command.
Fan / VFD direction command | u_MiscLEO2_WestUpperFwdCmd | Fan / VFD direction command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | MiscLEO2 | LEO equipment tag MiscLEO2; use BMS path for physical lookup. | /UAB2_BIO1/B4000_MiscLEO2_WestUpperFwdCmd | WestUpperFwdCmd | West Upper Fwd Cmd; Cmd=Command | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 19409 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCLEO2_WESTUPPERFWDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE COMMAND | trueText=s:Run¦falseText=s:Stop¦range=E:bacnet:BacnetBinaryPv |  | 2024-04-10 | 2026-04-27 | 247 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO2_WESTUPPERFWDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO2_WESTUPPERFWDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCLEO2_WESTUPPERFWDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD direction command.
Fan / VFD direction command | u_MiscLEO2_WestUpperRevCmd | Fan / VFD direction command | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | MiscLEO2 | LEO equipment tag MiscLEO2; use BMS path for physical lookup. | /UAB2_BIO1/B4000_MiscLEO2_WestUpperRevCmd | WestUpperRevCmd | West Upper Rev Cmd; Cmd=Command | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 19410 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCLEO2_WESTUPPERREVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE COMMAND | trueText=s:Run¦falseText=s:Stop¦range=E:bacnet:BacnetBinaryPv |  | 2024-04-10 | 2026-04-27 | 301 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO2_WESTUPPERREVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO2_WESTUPPERREVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCLEO2_WESTUPPERREVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD direction command.
Fan / VFD speed control | u_MiscLEO2_WestLowerFanSpd | Fan / VFD speed control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | MiscLEO2 | LEO equipment tag MiscLEO2; use BMS path for physical lookup. | /UAB2_BIO1/B4000_MiscLEO2_WestLowerFanSpd | WestLowerFanSpd | West Lower Fan Spd; Spd=Speed | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 19402 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCLEO2_WESTLOWERFANSPD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1 | Fan Speed | 2024-04-10 | present | 71469 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO2_WESTLOWERFANSPD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO2_WESTLOWERFANSPD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCLEO2_WESTLOWERFANSPD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Fan / VFD speed control | u_MiscLEO2_WestLowerSpdCmd | Fan / VFD speed control | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | MiscLEO2 | LEO equipment tag MiscLEO2; use BMS path for physical lookup. | /UAB2_BIO1/B4000_MiscLEO2_WestLowerSpdCmd | WestLowerSpdCmd | West Lower Spd Cmd; Cmd=Command; Spd=Speed | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 19405 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCLEO2_WESTLOWERSPDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1 | Fan cmd | 2024-04-10 | present | 71469 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO2_WESTLOWERSPDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO2_WESTLOWERSPDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCLEO2_WESTLOWERSPDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Fan / VFD speed control | u_MiscLEO2_WestUpperFanSpd | Fan / VFD speed control | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | LEO | Inventory BIOM=3, BIOMNAME=LEO. | MiscLEO2 | LEO equipment tag MiscLEO2; use BMS path for physical lookup. | /UAB2_BIO1/B4000_MiscLEO2_WestUpperFanSpd | WestUpperFanSpd | West Upper Fan Spd; Spd=Speed | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 19408 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCLEO2_WESTUPPERFANSPD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1 | Fan Speed | 2024-04-10 | present | 71469 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO2_WESTUPPERFANSPD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO2_WESTUPPERFANSPD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCLEO2_WESTUPPERFANSPD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Fan / VFD speed control | u_MiscLEO2_WestUpperSpdCmd | Fan / VFD speed control | command | High - name is command/setpoint for named climate equipment | LEO | Inventory BIOM=3, BIOMNAME=LEO. | MiscLEO2 | LEO equipment tag MiscLEO2; use BMS path for physical lookup. | /UAB2_BIO1/B4000_MiscLEO2_WestUpperSpdCmd | WestUpperSpdCmd | West Upper Spd Cmd; Cmd=Command; Spd=Speed | Changes airflow, exchange, pressure balance, or mixing for LEO. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 19412 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCLEO2_WESTUPPERSPDCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1 | Fan cmd | 2024-04-10 | present | 71469 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO2_WESTUPPERSPDCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCLEO2_WESTUPPERSPDCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCLEO2_WESTUPPERSPDCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Pressure setpoint | u_HEX01_HxSupHiPsrSp | Pressure setpoint | setpoint | High - name is command/setpoint for named climate equipment | Ocean | Inventory BIOM=2, BIOMNAME=Ocean. | HEX01 | Ocean heat exchanger HEX01. | /UAB2_BIO1/B4000_HEX01_HxSupHiPsrSp | HxSupHiPsrSp | Hx Sup Hi Psr Sp; Psr=Pressure; Sup=Supply | Sets target pressure used by equipment serving Ocean. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 715 | BIO2CONTROLS | UAB2_BIO1_B4000_HEX01_HXSUPHIPSRSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | psi | Pa | p_Pa = VALUE * 6894.757 | SENSOR | units=u:pounds per square inch;psi;(m-1)(kg)(s-2);*6894.75729; | Pressure | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_HXSUPHIPSRSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE * 6894.757 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_HXSUPHIPSRSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_HEX01_HXSUPHIPSRSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pressure setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Pump command | u_HEX01_OceanPmpCmd | Pump command | command | High - name is command/setpoint for named climate equipment | Ocean | Inventory BIOM=2, BIOMNAME=Ocean. | HEX01 | Ocean heat exchanger HEX01. | /UAB2_BIO1/B4000_HEX01_OceanPmpCmd | OceanPmpCmd | Ocean Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving Ocean or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 706 | BIO2CONTROLS | UAB2_BIO1_B4000_HEX01_OCEANPMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 824 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_OCEANPMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_OCEANPMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_HEX01_OCEANPMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command.
System enable | u_HEX01_SysEnable | System enable | command | High - name is command/setpoint for named climate equipment | Ocean | Inventory BIOM=2, BIOMNAME=Ocean. | HEX01 | Ocean heat exchanger HEX01. | /UAB2_BIO1/B4000_HEX01_SysEnable | SysEnable | Sys Enable | Potential control input affecting Ocean; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 699 | BIO2CONTROLS | UAB2_BIO1_B4000_HEX01_SYSENABLE | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-14 | 106 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_SYSENABLE live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_SYSENABLE t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_HEX01_SYSENABLE | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: System enable.
Temperature setpoint | u_HEX01_ActiveTmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Ocean | Inventory BIOM=2, BIOMNAME=Ocean. | HEX01 | Ocean heat exchanger HEX01. | /UAB2_BIO1/B4000_HEX01_ActiveTmpSp | ActiveTmpSp | Active Tmp Sp; Tmp=Temperature | Sets target temperature used by equipment serving Ocean. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 734 | BIO2CONTROLS | UAB2_BIO1_B4000_HEX01_ACTIVETMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_ACTIVETMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_ACTIVETMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_HEX01_ACTIVETMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_HEX01_DeltaTmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Ocean | Inventory BIOM=2, BIOMNAME=Ocean. | HEX01 | Ocean heat exchanger HEX01. | /UAB2_BIO1/B4000_HEX01_DeltaTmpSp | DeltaTmpSp | Delta Tmp Sp; Tmp=Temperature | Sets target temperature used by equipment serving Ocean. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 731 | BIO2CONTROLS | UAB2_BIO1_B4000_HEX01_DELTATMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_DELTATMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_DELTATMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_HEX01_DELTATMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_HEX01_OceanTmpSp | Temperature setpoint | setpoint | High - name is command/setpoint for named climate equipment | Ocean | Inventory BIOM=2, BIOMNAME=Ocean. | HEX01 | Ocean heat exchanger HEX01. | /UAB2_BIO1/B4000_HEX01_OceanTmpSp | OceanTmpSp | Ocean Tmp Sp; Tmp=Temperature | Sets target temperature used by equipment serving Ocean. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 702 | BIO2CONTROLS | UAB2_BIO1_B4000_HEX01_OCEANTMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_OCEANTMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_OCEANTMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_HEX01_OCEANTMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_HEX01_CHWVlvOut | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Ocean | Inventory BIOM=2, BIOMNAME=Ocean. | HEX01 | Ocean heat exchanger HEX01. | /UAB2_BIO1/B4000_HEX01_CHWVlvOut | CHWVlvOut | CHWVlv Out; CHW=Chill Water; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Ocean. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 732 | BIO2CONTROLS | UAB2_BIO1_B4000_HEX01_CHWVLVOUT | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_CHWVLVOUT live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_CHWVLVOUT t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_HEX01_CHWVLVOUT | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_HEX01_ChwVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Ocean | Inventory BIOM=2, BIOMNAME=Ocean. | HEX01 | Ocean heat exchanger HEX01. | /UAB2_BIO1/B4000_HEX01_ChwVlvPos | ChwVlvPos | Chw Vlv Pos; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Ocean. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 733 | BIO2CONTROLS | UAB2_BIO1_B4000_HEX01_CHWVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_CHWVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_CHWVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_HEX01_CHWVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_HEX01_HWVlvOut | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Ocean | Inventory BIOM=2, BIOMNAME=Ocean. | HEX01 | Ocean heat exchanger HEX01. | /UAB2_BIO1/B4000_HEX01_HWVlvOut | HWVlvOut | HWVlv Out; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Ocean. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 730 | BIO2CONTROLS | UAB2_BIO1_B4000_HEX01_HWVLVOUT | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_HWVLVOUT live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_HWVLVOUT t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_HEX01_HWVLVOUT | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_HEX01_HXRetVlvCmd | Valve command / position | command | High - name is command/setpoint for named climate equipment | Ocean | Inventory BIOM=2, BIOMNAME=Ocean. | HEX01 | Ocean heat exchanger HEX01. | /UAB2_BIO1/B4000_HEX01_HXRetVlvCmd | HXRetVlvCmd | HXRet Vlv Cmd; Cmd=Command; Ret=Return; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Ocean. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 725 | BIO2CONTROLS | UAB2_BIO1_B4000_HEX01_HXRETVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE COMMAND | trueText=s:HW¦falseText=s:CHW¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 5010 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_HXRETVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_HXRETVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_HEX01_HXRETVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position.
Valve command / position | u_HEX01_HXSupVlvCmd | Valve command / position | command | High - name is command/setpoint for named climate equipment | Ocean | Inventory BIOM=2, BIOMNAME=Ocean. | HEX01 | Ocean heat exchanger HEX01. | /UAB2_BIO1/B4000_HEX01_HXSupVlvCmd | HXSupVlvCmd | HXSup Vlv Cmd; Cmd=Command; Sup=Supply; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Ocean. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 720 | BIO2CONTROLS | UAB2_BIO1_B4000_HEX01_HXSUPVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE COMMAND | trueText=s:HW¦falseText=s:CHW¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 5005 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_HXSUPVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_HXSUPVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_HEX01_HXSUPVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position.
Valve command / position | u_HEX01_HwVlvPos | Valve command / position | actuator output / position feedback | Medium - actuator output/feedback, not necessarily operator-entered | Ocean | Inventory BIOM=2, BIOMNAME=Ocean. | HEX01 | Ocean heat exchanger HEX01. | /UAB2_BIO1/B4000_HEX01_HwVlvPos | HwVlvPos | Hw Vlv Pos; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving Ocean. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 714 | BIO2CONTROLS | UAB2_BIO1_B4000_HEX01_HWVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-22 | present | 149089 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_HWVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_HEX01_HWVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_HEX01_HWVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - actuator output/feedback, not necessarily operator-entered Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Level / height setpoint | u_MiscDES1_SLungWtrLvlSp | Level / height setpoint | setpoint | High - name is command/setpoint for named climate equipment | South lung | Inventory BIOM=8, BIOMNAME=South lung. | MiscDES1 | South lung miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES1_SLungWtrLvlSp | SLungWtrLvlSp | SLung Wtr Lvl Sp; Lvl=Level | Sets water level or height target for South lung support equipment. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 661 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES1_SLUNGWTRLVLSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | in | m | h_m = VALUE * 0.0254 | SENSOR | units=u:inch;in;(m);*0.0254; | Water level | 2022-01-22 | present | 149090 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SLUNGWTRLVLSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE * 0.0254 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES1_SLUNGWTRLVLSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES1_SLUNGWTRLVLSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Level / height setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Exhaust fan command | u_MiscDES2_SLungExhNCmd | Exhaust fan command | command | High - name is command/setpoint for named climate equipment | South lung | Inventory BIOM=8, BIOMNAME=South lung. | MiscDES2 | South lung miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES2_SLungExhNCmd | SLungExhNCmd | SLung Exh NCmd; Cmd=Command; Exh=Exhaust | Changes airflow, exchange, pressure balance, or mixing for South lung. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 626 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES2_SLUNGEXHNCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2022-02-26 | 2026-05-01 | 118801 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES2_SLUNGEXHNCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES2_SLUNGEXHNCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES2_SLUNGEXHNCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Exhaust fan command.
Exhaust fan command | u_MiscDES2_SLungExhSCmd | Exhaust fan command | command | High - name is command/setpoint for named climate equipment | South lung | Inventory BIOM=8, BIOMNAME=South lung. | MiscDES2 | South lung miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES2_SLungExhSCmd | SLungExhSCmd | SLung Exh SCmd; Cmd=Command; Exh=Exhaust | Changes airflow, exchange, pressure balance, or mixing for South lung. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 624 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES2_SLUNGEXHSCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2022-02-26 | 2026-05-01 | 119420 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES2_SLUNGEXHSCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES2_SLUNGEXHSCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES2_SLUNGEXHSCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Exhaust fan command.
Fan / VFD speed control | u_MiscDES2_SLungInjFanCmd | Fan / VFD speed control | command | High - name is command/setpoint for named climate equipment | South lung | Inventory BIOM=8, BIOMNAME=South lung. | MiscDES2 | South lung miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES2_SLungInjFanCmd | SLungInjFanCmd | SLung Inj Fan Cmd; Cmd=Command; Inj=Injection | Changes airflow, exchange, pressure balance, or mixing for South lung. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 620 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES2_SLUNGINJFANCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-19 | 282 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES2_SLUNGINJFANCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES2_SLUNGINJFANCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES2_SLUNGINJFANCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control.
Level / height setpoint | u_MiscDES2_SLungHeightSp | Level / height setpoint | setpoint | High - name is command/setpoint for named climate equipment | South lung | Inventory BIOM=8, BIOMNAME=South lung. | MiscDES2 | South lung miscellaneous climate controls; verify exact field device from BMS path. | /UAB2_BIO1/B4000_MiscDES2_SLungHeightSp | SLungHeightSp | SLung Height Sp | Sets water level or height target for South lung support equipment. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 621 | BIO2CONTROLS | UAB2_BIO1_B4000_MISCDES2_SLUNGHEIGHTSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | in | m | h_m = VALUE * 0.0254 | SENSOR | units=u:inch;in;(m);*0.0254; | Height | 2022-01-22 | present | 149090 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES2_SLUNGHEIGHTSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE * 0.0254 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_MISCDES2_SLUNGHEIGHTSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_MISCDES2_SLUNGHEIGHTSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Level / height setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Pressure setpoint | u_WaveWall_HiPsrSpt | Pressure setpoint | setpoint | High - name is command/setpoint for named climate equipment | Wave wall | Inventory BIOM=9, BIOMNAME=Wave wall. | WaveWall | Wave wall controls. | /UAB2_BIO1/B4000_WaveWall_HiPsrSpt | HiPsrSpt | High Pressure Setpoint | Sets target pressure used by equipment serving Wave wall. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 476 | BIO2CONTROLS | UAB2_BIO1_B4000_WAVEWALL_HIPSRSPT | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | inH2O | m water | h_m = VALUE * 0.0254 | SENSOR | units=u:inches of water;in/wc;(m-1)(kg)(s-2);*248.84;¦precision=i:1 | Water level | 2022-01-22 | present | 149090 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_WAVEWALL_HIPSRSPT live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE * 0.0254 AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_WAVEWALL_HIPSRSPT t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_WAVEWALL_HIPSRSPT | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pressure setpoint. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
System enable | u_WaveWall_Enable | System enable | command | High - name is command/setpoint for named climate equipment | Wave wall | Inventory BIOM=9, BIOMNAME=Wave wall. | WaveWall | Wave wall controls. | /UAB2_BIO1/B4000_WaveWall_Enable | Enable | Enable | Potential control input affecting Wave wall; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 480 | BIO2CONTROLS | UAB2_BIO1_B4000_WAVEWALL_ENABLE | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE COMMAND | trueText=s:ENABLED¦falseText=s:DISABLED¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 963 | Yes - BIO2CONTROLS.UAB2_BIO1_B4000_WAVEWALL_ENABLE live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_BIO1_B4000_WAVEWALL_ENABLE t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_BIO1_B4000_WAVEWALL_ENABLE | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: System enable.
Boiler command / setpoint | u_BLRF1A_BlrCmd | Boiler command / setpoint | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | BLRF1A | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_BLRF1A_BlrCmd | BlrCmd | Blr Cmd; Blr=Boiler; Cmd=Command | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 6 | BIO2CONTROLS | UAB2_EC1_B4008_BLRF1A_BLRCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 1002 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_BLRF1A_BLRCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_BLRF1A_BLRCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_BLRF1A_BLRCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Isolation valve command | u_BLRF1A_IsoVlvCmd | Isolation valve command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | BLRF1A | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_BLRF1A_IsoVlvCmd | IsoVlvCmd | Iso Vlv Cmd; Cmd=Command; Iso=Isolation; Vlv=Valve | Changes hydronic/air/water flow through equipment serving EC. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 10 | BIO2CONTROLS | UAB2_EC1_B4008_BLRF1A_ISOVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 816 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_BLRF1A_ISOVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_BLRF1A_ISOVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_BLRF1A_ISOVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Isolation valve command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Boiler command / setpoint | u_BLRF1B_BlrCmd | Boiler command / setpoint | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | BLRF1B | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_BLRF1B_BlrCmd | BlrCmd | Blr Cmd; Blr=Boiler; Cmd=Command | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 12 | BIO2CONTROLS | UAB2_EC1_B4008_BLRF1B_BLRCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 319 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_BLRF1B_BLRCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_BLRF1B_BLRCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_BLRF1B_BLRCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Valve command / position | u_CHEM_BrominatorVlvCmd | Valve command / position | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHEM | EC equipment tag CHEM; use BMS path for physical lookup. | /UAB2_EC1/B4008_CHEM_BrominatorVlvCmd | BrominatorVlvCmd | Brominator Vlv Cmd; Cmd=Command; Vlv=Valve | Changes hydronic/air/water flow through equipment serving EC. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 29 | BIO2CONTROLS | UAB2_EC1_B4008_CHEM_BROMINATORVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | VALVE STATUS | trueText=s:OPEN¦falseText=s:CLOSE¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-03-17 | 675 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHEM_BROMINATORVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHEM_BROMINATORVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHEM_BROMINATORVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_CHEMP20_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHEMP20 | EC equipment tag CHEMP20; use BMS path for physical lookup. | /UAB2_EC1/B4008_CHEMP20_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 16 | BIO2CONTROLS | UAB2_EC1_B4008_CHEMP20_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-10 | 728 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHEMP20_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHEMP20_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHEMP20_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_CHEMP21_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHEMP21 | EC equipment tag CHEMP21; use BMS path for physical lookup. | /UAB2_EC1/B4008_CHEMP21_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 21 | BIO2CONTROLS | UAB2_EC1_B4008_CHEMP21_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-12 | 738 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHEMP21_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHEMP21_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHEMP21_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_CHEMP22_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHEMP22 | EC equipment tag CHEMP22; use BMS path for physical lookup. | /UAB2_EC1/B4008_CHEMP22_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 25 | BIO2CONTROLS | UAB2_EC1_B4008_CHEMP22_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-13 | 732 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHEMP22_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHEMP22_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHEMP22_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Chiller command / setpoint | u_CHLR3B_ChlrCmd | Chiller command / setpoint | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHLR3B | Energy Center chiller/cold-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_CHLR3B_ChlrCmd | ChlrCmd | Chlr Cmd; Chlr=Chiller; Cmd=Command | Changes cooling capacity available to EC or to the shared chilled-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 36 | BIO2CONTROLS | UAB2_EC1_B4008_CHLR3B_CHLRCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 8113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHLR3B_CHLRCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHLR3B_CHLRCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHLR3B_CHLRCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Chiller command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Level / height setpoint | u_CHLR3B_RefLvlSp | Level / height setpoint | setpoint | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHLR3B | Energy Center chiller/cold-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_CHLR3B_RefLvlSp | RefLvlSp | Ref Lvl Sp; Lvl=Level | Sets water level or height target for EC support equipment. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 61 | BIO2CONTROLS | UAB2_EC1_B4008_CHLR3B_REFLVLSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | Level SENSOR (unit-less) | units=u:null;;;;¦precision=i:1¦min=d:-inf¦max=d:+inf |  | 2022-01-08 | present | 151114 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHLR3B_REFLVLSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHLR3B_REFLVLSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHLR3B_REFLVLSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Level / height setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Temperature setpoint | u_CHLR3B_CWSTmpSp | Temperature setpoint | setpoint | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHLR3B | Energy Center chiller/cold-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_CHLR3B_CWSTmpSp | CWSTmpSp | CWSTmp Sp; CWS=Cold Water supply; Tmp=Temperature | Sets target temperature used by equipment serving EC. | Thermal boundary-control parameter | Use as known actuator trajectory or estimate an actuator-to-boundary map for heat flux/air temperature. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 37 | BIO2CONTROLS | UAB2_EC1_B4008_CHLR3B_CWSTMPSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-08 | present | 151114 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHLR3B_CWSTMPSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHLR3B_CWSTMPSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHLR3B_CWSTMPSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Temperature setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_CHLR3B_HPVlvOut | Valve command / position | actuator output / position feedback | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHLR3B | Energy Center chiller/cold-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_CHLR3B_HPVlvOut | HPVlvOut | HPVlv Out; Vlv=Valve | Changes hydronic/air/water flow through equipment serving EC. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 49 | BIO2CONTROLS | UAB2_EC1_B4008_CHLR3B_HPVLVOUT | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-08 | present | 151114 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHLR3B_HPVLVOUT live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHLR3B_HPVLVOUT t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHLR3B_HPVLVOUT | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Valve command / position | u_CHLR3B_MinVlvPos | Valve command / position | actuator output / position feedback | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHLR3B | Energy Center chiller/cold-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_CHLR3B_MinVlvPos | MinVlvPos | Min Vlv Pos; Min=Minimum; Pos=Position; Vlv=Valve | Changes hydronic/air/water flow through equipment serving EC. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 52 | BIO2CONTROLS | UAB2_EC1_B4008_CHLR3B_MINVLVPOS | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-08 | present | 151114 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHLR3B_MINVLVPOS live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHLR3B_MINVLVPOS t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHLR3B_MINVLVPOS | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Pump command | u_CHWP14A_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHWP14A | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_CHWP14A_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 67 | BIO2CONTROLS | UAB2_EC1_B4008_CHWP14A_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-04 | 223 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHWP14A_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHWP14A_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHWP14A_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_CHWP17A_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHWP17A | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_CHWP17A_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 68 | BIO2CONTROLS | UAB2_EC1_B4008_CHWP17A_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 560 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHWP17A_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHWP17A_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHWP17A_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_CHWP17B_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHWP17B | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_CHWP17B_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 71 | BIO2CONTROLS | UAB2_EC1_B4008_CHWP17B_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 533 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHWP17B_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHWP17B_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHWP17B_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_CHWP17C_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHWP17C | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_CHWP17C_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 72 | BIO2CONTROLS | UAB2_EC1_B4008_CHWP17C_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 1106 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHWP17C_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHWP17C_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHWP17C_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_CHWP6B_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHWP6B | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_CHWP6B_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 76 | BIO2CONTROLS | UAB2_EC1_B4008_CHWP6B_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 4769 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHWP6B_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHWP6B_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHWP6B_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_CHWP8A_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHWP8A | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_CHWP8A_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 79 | BIO2CONTROLS | UAB2_EC1_B4008_CHWP8A_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 396 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHWP8A_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHWP8A_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHWP8A_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_CHWP8B_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHWP8B | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_CHWP8B_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 80 | BIO2CONTROLS | UAB2_EC1_B4008_CHWP8B_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 884 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHWP8B_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHWP8B_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHWP8B_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_CHWP8C_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHWP8C | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_CHWP8C_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 82 | BIO2CONTROLS | UAB2_EC1_B4008_CHWP8C_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 481 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHWP8C_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHWP8C_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHWP8C_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Valve command / position | u_CHWVT61_VlvCmd | Valve command / position | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHWVT61 | Energy Center hydronic/tower-water valve or loop equipment; downstream loop should be verified. | /UAB2_EC1/B4008_CHWVT61_VlvCmd | VlvCmd | Vlv Cmd; Cmd=Command; Vlv=Valve | Changes hydronic/air/water flow through equipment serving EC. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 91 | BIO2CONTROLS | UAB2_EC1_B4008_CHWVT61_VLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | VALVE STATUS | trueText=s:OPEN¦falseText=s:CLOSE¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-15 | 269 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHWVT61_VLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHWVT61_VLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHWVT61_VLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Valve command / position | u_CHWVT62_VlvCmd | Valve command / position | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CHWVT62 | Energy Center hydronic/tower-water valve or loop equipment; downstream loop should be verified. | /UAB2_EC1/B4008_CHWVT62_VlvCmd | VlvCmd | Vlv Cmd; Cmd=Command; Vlv=Valve | Changes hydronic/air/water flow through equipment serving EC. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 94 | BIO2CONTROLS | UAB2_EC1_B4008_CHWVT62_VLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | VALVE STATUS | trueText=s:OPEN¦falseText=s:CLOSE¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-15 | 47 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CHWVT62_VLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CHWVT62_VLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CHWVT62_VLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Compressor run command | u_COMPC1_RunCmd | Compressor run command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | COMPC1 | Energy Center compressor equipment; downstream function should be verified. | /UAB2_EC1/B4008_COMPC1_RunCmd | RunCmd | Run Cmd; Cmd=Command | Potential control input affecting EC; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 100 | BIO2CONTROLS | UAB2_EC1_B4008_COMPC1_RUNCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-04 | 393 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_COMPC1_RUNCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_COMPC1_RUNCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_COMPC1_RUNCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Compressor run command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Compressor run command | u_COMPC3A_RunCmd | Compressor run command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | COMPC3A | Energy Center compressor equipment; downstream function should be verified. | /UAB2_EC1/B4008_COMPC3A_RunCmd | RunCmd | Run Cmd; Cmd=Command | Potential control input affecting EC; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 99 | BIO2CONTROLS | UAB2_EC1_B4008_COMPC3A_RUNCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-04 | 262 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_COMPC3A_RUNCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_COMPC3A_RUNCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_COMPC3A_RUNCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Compressor run command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Compressor run command | u_COMPC3B_RunCmd | Compressor run command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | COMPC3B | Energy Center compressor equipment; downstream function should be verified. | /UAB2_EC1/B4008_COMPC3B_RunCmd | RunCmd | Run Cmd; Cmd=Command | Potential control input affecting EC; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 104 | BIO2CONTROLS | UAB2_EC1_B4008_COMPC3B_RUNCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-03-26 | 257 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_COMPC3B_RUNCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_COMPC3B_RUNCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_COMPC3B_RUNCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Compressor run command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Control parameter / needs classification | u_CPF1B_Cmd | Control parameter / needs classification | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CPF1B | EC equipment tag CPF1B; use BMS path for physical lookup. | /UAB2_EC1/B4008_CPF1B_Cmd | Cmd | Command | Potential control input affecting EC; physical pathway needs verification. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 106 | BIO2CONTROLS | UAB2_EC1_B4008_CPF1B_CMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-04 | 276 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CPF1B_CMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CPF1B_CMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CPF1B_CMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Control parameter / needs classification. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Fan / VFD speed control | u_CTH1A_FanSpd | Fan / VFD speed control | actuator output / position feedback | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CTH1A | Energy Center VFD or cooling-tower fan equipment; downstream loop should be verified. | /UAB2_EC1/B4008_CTH1A_FanSpd | FanSpd | Fan Spd; Spd=Speed | Changes airflow, exchange, pressure balance, or mixing for EC. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 451 | BIO2CONTROLS | UAB2_EC1_B4008_CTH1A_FANSPD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1 |  | 2022-04-29 | present | 140488 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CTH1A_FANSPD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CTH1A_FANSPD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CTH1A_FANSPD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Isolation valve command | u_CTH1A_IsoVlvCmd | Isolation valve command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CTH1A | Energy Center VFD or cooling-tower fan equipment; downstream loop should be verified. | /UAB2_EC1/B4008_CTH1A_IsoVlvCmd | IsoVlvCmd | Iso Vlv Cmd; Cmd=Command; Iso=Isolation; Vlv=Valve | Changes hydronic/air/water flow through equipment serving EC. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 108 | BIO2CONTROLS | UAB2_EC1_B4008_CTH1A_ISOVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | VALVE COMMAND | trueText=s:Open¦falseText=s:Closed¦range=E:bacnet:BacnetBinaryPv |  | 2022-01-13 | 2026-05-01 | 8449 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CTH1A_ISOVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CTH1A_ISOVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CTH1A_ISOVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Isolation valve command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Fan / VFD speed control | u_CTH1B_FanCmdHi | Fan / VFD speed control | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CTH1B | Energy Center VFD or cooling-tower fan equipment; downstream loop should be verified. | /UAB2_EC1/B4008_CTH1B_FanCmdHi | FanCmdHi | Fan Cmd Hi; Cmd=Command | Changes airflow, exchange, pressure balance, or mixing for EC. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 110 | BIO2CONTROLS | UAB2_EC1_B4008_CTH1B_FANCMDHI | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 7852 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CTH1B_FANCMDHI live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CTH1B_FANCMDHI t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CTH1B_FANCMDHI | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Fan / VFD speed control | u_CTH1B_FanCmdLo | Fan / VFD speed control | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CTH1B | Energy Center VFD or cooling-tower fan equipment; downstream loop should be verified. | /UAB2_EC1/B4008_CTH1B_FanCmdLo | FanCmdLo | Fan Cmd Lo; Cmd=Command | Changes airflow, exchange, pressure balance, or mixing for EC. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 113 | BIO2CONTROLS | UAB2_EC1_B4008_CTH1B_FANCMDLO | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 1514 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CTH1B_FANCMDLO live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CTH1B_FANCMDLO t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CTH1B_FANCMDLO | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Fan / VFD speed control | u_CTH1B_FanCmdOff | Fan / VFD speed control | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CTH1B | Energy Center VFD or cooling-tower fan equipment; downstream loop should be verified. | /UAB2_EC1/B4008_CTH1B_FanCmdOff | FanCmdOff | Fan Cmd Off; Cmd=Command | Changes airflow, exchange, pressure balance, or mixing for EC. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 112 | BIO2CONTROLS | UAB2_EC1_B4008_CTH1B_FANCMDOFF | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 15625 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CTH1B_FANCMDOFF live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CTH1B_FANCMDOFF t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CTH1B_FANCMDOFF | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Isolation valve command | u_CTH1B_IsoVlvCmd | Isolation valve command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CTH1B | Energy Center VFD or cooling-tower fan equipment; downstream loop should be verified. | /UAB2_EC1/B4008_CTH1B_IsoVlvCmd | IsoVlvCmd | Iso Vlv Cmd; Cmd=Command; Iso=Isolation; Vlv=Valve | Changes hydronic/air/water flow through equipment serving EC. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 116 | BIO2CONTROLS | UAB2_EC1_B4008_CTH1B_ISOVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | VALVE COMMAND | trueText=s:Open¦falseText=s:Closed¦range=E:bacnet:BacnetBinaryPv |  | 2022-01-13 | 2026-05-01 | 15429 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CTH1B_ISOVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CTH1B_ISOVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CTH1B_ISOVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Isolation valve command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Fan / VFD speed control | u_CTH1C_FanSpd | Fan / VFD speed control | actuator output / position feedback | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CTH1C | Energy Center VFD or cooling-tower fan equipment; downstream loop should be verified. | /UAB2_EC1/B4008_CTH1C_FanSpd | FanSpd | Fan Spd; Spd=Speed | Changes airflow, exchange, pressure balance, or mixing for EC. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 452 | BIO2CONTROLS | UAB2_EC1_B4008_CTH1C_FANSPD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;;¦precision=i:1 |  | 2022-04-29 | present | 140488 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CTH1C_FANSPD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CTH1C_FANSPD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CTH1C_FANSPD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Isolation valve command | u_CTH1C_IsoVlvCmd | Isolation valve command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CTH1C | Energy Center VFD or cooling-tower fan equipment; downstream loop should be verified. | /UAB2_EC1/B4008_CTH1C_IsoVlvCmd | IsoVlvCmd | Iso Vlv Cmd; Cmd=Command; Iso=Isolation; Vlv=Valve | Changes hydronic/air/water flow through equipment serving EC. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 120 | BIO2CONTROLS | UAB2_EC1_B4008_CTH1C_ISOVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | VALVE COMMAND | trueText=s:Open¦falseText=s:Closed¦range=E:bacnet:BacnetBinaryPv |  | 2022-01-13 | 2026-05-01 | 8050 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CTH1C_ISOVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CTH1C_ISOVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CTH1C_ISOVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Isolation valve command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Valve command / position | u_CVCHR3_VlvCmd | Valve command / position | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CVCHR3 | Energy Center hydronic/tower-water valve or loop equipment; downstream loop should be verified. | /UAB2_EC1/B4008_CVCHR3_VlvCmd | VlvCmd | Vlv Cmd; Cmd=Command; Vlv=Valve | Changes hydronic/air/water flow through equipment serving EC. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 122 | BIO2CONTROLS | UAB2_EC1_B4008_CVCHR3_VLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | VALVE STATUS | trueText=s:OPEN¦falseText=s:CLOSE¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-04 | 374 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CVCHR3_VLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CVCHR3_VLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CVCHR3_VLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Valve command / position | u_CVCHS1_VlvCmd | Valve command / position | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CVCHS1 | Energy Center hydronic/tower-water valve or loop equipment; downstream loop should be verified. | /UAB2_EC1/B4008_CVCHS1_VlvCmd | VlvCmd | Vlv Cmd; Cmd=Command; Vlv=Valve | Changes hydronic/air/water flow through equipment serving EC. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 124 | BIO2CONTROLS | UAB2_EC1_B4008_CVCHS1_VLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | VALVE STATUS | trueText=s:OPEN¦falseText=s:CLOSE¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-03-30 | 315 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CVCHS1_VLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CVCHS1_VLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CVCHS1_VLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Valve command / position | u_CVCHS2_VlvCmd | Valve command / position | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CVCHS2 | Energy Center hydronic/tower-water valve or loop equipment; downstream loop should be verified. | /UAB2_EC1/B4008_CVCHS2_VlvCmd | VlvCmd | Vlv Cmd; Cmd=Command; Vlv=Valve | Changes hydronic/air/water flow through equipment serving EC. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 123 | BIO2CONTROLS | UAB2_EC1_B4008_CVCHS2_VLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | VALVE STATUS | trueText=s:OPEN¦falseText=s:CLOSE¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-30 | 4520 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CVCHS2_VLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CVCHS2_VLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CVCHS2_VLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Valve command / position | u_CVP6B_Cmd | Valve command / position | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CVP6B | Energy Center hydronic/tower-water valve or loop equipment; downstream loop should be verified. | /UAB2_EC1/B4008_CVP6B_Cmd | Cmd | Command | Changes hydronic/air/water flow through equipment serving EC. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 125 | BIO2CONTROLS | UAB2_EC1_B4008_CVP6B_CMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | VALVE STATUS | trueText=s:OPEN¦falseText=s:CLOSE¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-03-26 | 378 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CVP6B_CMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CVP6B_CMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CVP6B_CMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Valve command / position | u_CVR3B1_VlvCmd | Valve command / position | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | CVR3B1 | Energy Center hydronic/tower-water valve or loop equipment; downstream loop should be verified. | /UAB2_EC1/B4008_CVR3B1_VlvCmd | VlvCmd | Vlv Cmd; Cmd=Command; Vlv=Valve | Changes hydronic/air/water flow through equipment serving EC. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 127 | BIO2CONTROLS | UAB2_EC1_B4008_CVR3B1_VLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | VALVE STATUS | trueText=s:OPEN¦falseText=s:CLOSE¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-03-26 | 2299 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_CVR3B1_VLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_CVR3B1_VLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_CVR3B1_VLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Boiler command / setpoint | u_F1A1_BlrEnable | Boiler command / setpoint | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A1 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A1_BlrEnable | BlrEnable | Blr Enable; Blr=Boiler | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 140 | BIO2CONTROLS | UAB2_EC1_B4008_F1A1_BLRENABLE | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS | trueText=s:Active¦falseText=s:Inactive¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 1323 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A1_BLRENABLE live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A1_BLRENABLE t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A1_BLRENABLE | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Boiler command / setpoint | u_F1A1_BlrFiringRat | Boiler command / setpoint | needs engineering verification | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A1 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A1_BlrFiringRat | BlrFiringRat | Blr Firing Rat; FiringRat=Firing Rate; Blr=Boiler | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 142 | BIO2CONTROLS | UAB2_EC1_B4008_F1A1_BLRFIRINGRAT | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A1_BLRFIRINGRAT live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A1_BLRFIRINGRAT t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A1_BLRFIRINGRAT | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Boiler command / setpoint | u_F1A1_BlrFlameCmd | Boiler command / setpoint | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A1 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A1_BlrFlameCmd | BlrFlameCmd | Blr Flame Cmd; Blr=Boiler; Cmd=Command | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 144 | BIO2CONTROLS | UAB2_EC1_B4008_F1A1_BLRFLAMECMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | V | V | value_si = raw VALUE | SENSOR | units=u:volt;V;(m2)(kg)(s-3)(A-1);; | Voltage | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A1_BLRFLAMECMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A1_BLRFLAMECMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A1_BLRFLAMECMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Boiler command / setpoint | u_F1A1_BlrSp_Read | Boiler command / setpoint | needs engineering verification | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A1 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A1_BlrSp_Read | BlrSp_Read | Blr Sp Read; Blr=Boiler | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 147 | BIO2CONTROLS | UAB2_EC1_B4008_F1A1_BLRSP_READ | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A1_BLRSP_READ live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A1_BLRSP_READ t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A1_BLRSP_READ | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Boiler efficiency setpoint | u_F1A1_EffSp | Boiler efficiency setpoint | setpoint | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A1 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A1_EffSp | EffSp | EfficiencySetpoint | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 150 | BIO2CONTROLS | UAB2_EC1_B4008_F1A1_EFFSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A1_EFFSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A1_EFFSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A1_EFFSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler efficiency setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Fan / VFD speed control | u_F1A1_BlrFanSpd | Fan / VFD speed control | actuator output / position feedback | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A1 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A1_BlrFanSpd | BlrFanSpd | Blr Fan Spd; Blr=Boiler; Spd=Speed | Changes airflow, exchange, pressure balance, or mixing for EC. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 143 | BIO2CONTROLS | UAB2_EC1_B4008_F1A1_BLRFANSPD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | Level SENSOR (unit-less) | units=u:null;;;; |  | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A1_BLRFANSPD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A1_BLRFANSPD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A1_BLRFANSPD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Boiler command / setpoint | u_F1A2_BlrDmd | Boiler command / setpoint | controller demand | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A2 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A2_BlrDmd | BlrDmd | Blr Dmd; Blr=Boiler; Dmd=Demand | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 153 | BIO2CONTROLS | UAB2_EC1_B4008_F1A2_BLRDMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS | trueText=s:Active¦falseText=s:Inactive¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 628 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A2_BLRDMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A2_BLRDMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A2_BLRDMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Boiler command / setpoint | u_F1A2_BlrEnable | Boiler command / setpoint | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A2 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A2_BlrEnable | BlrEnable | Blr Enable; Blr=Boiler | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 156 | BIO2CONTROLS | UAB2_EC1_B4008_F1A2_BLRENABLE | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS | trueText=s:Active¦falseText=s:Inactive¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 941 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A2_BLRENABLE live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A2_BLRENABLE t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A2_BLRENABLE | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Boiler command / setpoint | u_F1A2_BlrFiringRat | Boiler command / setpoint | needs engineering verification | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A2 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A2_BlrFiringRat | BlrFiringRat | Blr Firing Rat; FiringRat=Firing Rate; Blr=Boiler | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 160 | BIO2CONTROLS | UAB2_EC1_B4008_F1A2_BLRFIRINGRAT | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A2_BLRFIRINGRAT live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A2_BLRFIRINGRAT t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A2_BLRFIRINGRAT | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Boiler command / setpoint | u_F1A2_BlrFlameCmd | Boiler command / setpoint | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A2 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A2_BlrFlameCmd | BlrFlameCmd | Blr Flame Cmd; Blr=Boiler; Cmd=Command | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 159 | BIO2CONTROLS | UAB2_EC1_B4008_F1A2_BLRFLAMECMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | V | V | value_si = raw VALUE | SENSOR | units=u:volt;V;(m2)(kg)(s-3)(A-1);; | Voltage | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A2_BLRFLAMECMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A2_BLRFLAMECMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A2_BLRFLAMECMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Boiler command / setpoint | u_F1A2_BlrSp | Boiler command / setpoint | setpoint | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A2 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A2_BlrSp | BlrSp | Blr Sp; Blr=Boiler | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 163 | BIO2CONTROLS | UAB2_EC1_B4008_F1A2_BLRSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A2_BLRSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A2_BLRSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A2_BLRSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Boiler efficiency setpoint | u_F1A2_EffSp | Boiler efficiency setpoint | setpoint | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A2 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A2_EffSp | EffSp | EfficiencySetpoint | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 168 | BIO2CONTROLS | UAB2_EC1_B4008_F1A2_EFFSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A2_EFFSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A2_EFFSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A2_EFFSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler efficiency setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Fan / VFD speed control | u_F1A2_BlrFanSpd | Fan / VFD speed control | actuator output / position feedback | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A2 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A2_BlrFanSpd | BlrFanSpd | Blr Fan Spd; Blr=Boiler; Spd=Speed | Changes airflow, exchange, pressure balance, or mixing for EC. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 157 | BIO2CONTROLS | UAB2_EC1_B4008_F1A2_BLRFANSPD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | Level SENSOR (unit-less) | units=u:null;;;; |  | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A2_BLRFANSPD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A2_BLRFANSPD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A2_BLRFANSPD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Boiler command / setpoint | u_F1A3_BlrDmd | Boiler command / setpoint | controller demand | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A3 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A3_BlrDmd | BlrDmd | Blr Dmd; Blr=Boiler; Dmd=Demand | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 169 | BIO2CONTROLS | UAB2_EC1_B4008_F1A3_BLRDMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS | trueText=s:Active¦falseText=s:Inactive¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 662 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A3_BLRDMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A3_BLRDMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A3_BLRDMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Boiler command / setpoint | u_F1A3_BlrEnable | Boiler command / setpoint | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A3 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A3_BlrEnable | BlrEnable | Blr Enable; Blr=Boiler | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 171 | BIO2CONTROLS | UAB2_EC1_B4008_F1A3_BLRENABLE | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS | trueText=s:Active¦falseText=s:Inactive¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 1000 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A3_BLRENABLE live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A3_BLRENABLE t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A3_BLRENABLE | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Boiler command / setpoint | u_F1A3_BlrFiringRat | Boiler command / setpoint | needs engineering verification | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A3 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A3_BlrFiringRat | BlrFiringRat | Blr Firing Rat; FiringRat=Firing Rate; Blr=Boiler | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 176 | BIO2CONTROLS | UAB2_EC1_B4008_F1A3_BLRFIRINGRAT | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A3_BLRFIRINGRAT live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A3_BLRFIRINGRAT t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A3_BLRFIRINGRAT | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Boiler command / setpoint | u_F1A3_BlrFlameCmd | Boiler command / setpoint | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A3 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A3_BlrFlameCmd | BlrFlameCmd | Blr Flame Cmd; Blr=Boiler; Cmd=Command | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 175 | BIO2CONTROLS | UAB2_EC1_B4008_F1A3_BLRFLAMECMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | V | V | value_si = raw VALUE | SENSOR | units=u:volt;V;(m2)(kg)(s-3)(A-1);; | Voltage | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A3_BLRFLAMECMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A3_BLRFLAMECMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A3_BLRFLAMECMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Boiler command / setpoint | u_F1A3_BlrSp | Boiler command / setpoint | setpoint | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A3 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A3_BlrSp | BlrSp | Blr Sp; Blr=Boiler | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 179 | BIO2CONTROLS | UAB2_EC1_B4008_F1A3_BLRSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A3_BLRSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A3_BLRSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A3_BLRSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Boiler efficiency setpoint | u_F1A3_EffSp | Boiler efficiency setpoint | setpoint | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A3 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A3_EffSp | EffSp | EfficiencySetpoint | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 183 | BIO2CONTROLS | UAB2_EC1_B4008_F1A3_EFFSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A3_EFFSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A3_EFFSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A3_EFFSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler efficiency setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Fan / VFD speed control | u_F1A3_BlrFanSpd | Fan / VFD speed control | actuator output / position feedback | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A3 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A3_BlrFanSpd | BlrFanSpd | Blr Fan Spd; Blr=Boiler; Spd=Speed | Changes airflow, exchange, pressure balance, or mixing for EC. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 174 | BIO2CONTROLS | UAB2_EC1_B4008_F1A3_BLRFANSPD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | Level SENSOR (unit-less) | units=u:null;;;; |  | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A3_BLRFANSPD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A3_BLRFANSPD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A3_BLRFANSPD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Boiler command / setpoint | u_F1A4_BlrDmd | Boiler command / setpoint | controller demand | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A4 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A4_BlrDmd | BlrDmd | Blr Dmd; Blr=Boiler; Dmd=Demand | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 186 | BIO2CONTROLS | UAB2_EC1_B4008_F1A4_BLRDMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS | trueText=s:Active¦falseText=s:Inactive¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 640 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A4_BLRDMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A4_BLRDMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A4_BLRDMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Boiler command / setpoint | u_F1A4_BlrEnable | Boiler command / setpoint | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A4 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A4_BlrEnable | BlrEnable | Blr Enable; Blr=Boiler | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 189 | BIO2CONTROLS | UAB2_EC1_B4008_F1A4_BLRENABLE | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS | trueText=s:Active¦falseText=s:Inactive¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 976 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A4_BLRENABLE live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A4_BLRENABLE t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A4_BLRENABLE | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Boiler command / setpoint | u_F1A4_BlrFiringRat | Boiler command / setpoint | needs engineering verification | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A4 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A4_BlrFiringRat | BlrFiringRat | Blr Firing Rat; FiringRat=Firing Rate; Blr=Boiler | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 191 | BIO2CONTROLS | UAB2_EC1_B4008_F1A4_BLRFIRINGRAT | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A4_BLRFIRINGRAT live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A4_BLRFIRINGRAT t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A4_BLRFIRINGRAT | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Boiler command / setpoint | u_F1A4_BlrFlameCmd | Boiler command / setpoint | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A4 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A4_BlrFlameCmd | BlrFlameCmd | Blr Flame Cmd; Blr=Boiler; Cmd=Command | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 192 | BIO2CONTROLS | UAB2_EC1_B4008_F1A4_BLRFLAMECMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | V | V | value_si = raw VALUE | SENSOR | units=u:volt;V;(m2)(kg)(s-3)(A-1);; | Voltage | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A4_BLRFLAMECMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A4_BLRFLAMECMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A4_BLRFLAMECMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Boiler command / setpoint | u_F1A4_BlrSp | Boiler command / setpoint | setpoint | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A4 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A4_BlrSp | BlrSp | Blr Sp; Blr=Boiler | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 194 | BIO2CONTROLS | UAB2_EC1_B4008_F1A4_BLRSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A4_BLRSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A4_BLRSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A4_BLRSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Boiler efficiency setpoint | u_F1A4_EffSp | Boiler efficiency setpoint | setpoint | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A4 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A4_EffSp | EffSp | EfficiencySetpoint | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 200 | BIO2CONTROLS | UAB2_EC1_B4008_F1A4_EFFSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A4_EFFSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A4_EFFSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A4_EFFSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler efficiency setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Fan / VFD speed control | u_F1A4_BlrFanSpd | Fan / VFD speed control | actuator output / position feedback | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A4 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A4_BlrFanSpd | BlrFanSpd | Blr Fan Spd; Blr=Boiler; Spd=Speed | Changes airflow, exchange, pressure balance, or mixing for EC. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 190 | BIO2CONTROLS | UAB2_EC1_B4008_F1A4_BLRFANSPD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | Level SENSOR (unit-less) | units=u:null;;;; |  | 2022-01-08 | present | 151113 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A4_BLRFANSPD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A4_BLRFANSPD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A4_BLRFANSPD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Boiler command / setpoint | u_F1A5_BlrDmd | Boiler command / setpoint | controller demand | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A5 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A5_BlrDmd | BlrDmd | Blr Dmd; Blr=Boiler; Dmd=Demand | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 202 | BIO2CONTROLS | UAB2_EC1_B4008_F1A5_BLRDMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS | trueText=s:Active¦falseText=s:Inactive¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 591 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A5_BLRDMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A5_BLRDMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A5_BLRDMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Boiler command / setpoint | u_F1A5_BlrEnable | Boiler command / setpoint | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A5 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A5_BlrEnable | BlrEnable | Blr Enable; Blr=Boiler | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 203 | BIO2CONTROLS | UAB2_EC1_B4008_F1A5_BLRENABLE | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS | trueText=s:Active¦falseText=s:Inactive¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 975 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A5_BLRENABLE live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A5_BLRENABLE t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A5_BLRENABLE | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Boiler command / setpoint | u_F1A5_BlrFiringRat | Boiler command / setpoint | needs engineering verification | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A5 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A5_BlrFiringRat | BlrFiringRat | Blr Firing Rat; FiringRat=Firing Rate; Blr=Boiler | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 208 | BIO2CONTROLS | UAB2_EC1_B4008_F1A5_BLRFIRINGRAT | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | % | fraction | value_si = VALUE / 100 | SENSOR | units=u:percent;%;;; |  | 2022-01-08 | present | 151112 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A5_BLRFIRINGRAT live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE / 100 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A5_BLRFIRINGRAT t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A5_BLRFIRINGRAT | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Boiler command / setpoint | u_F1A5_BlrFlameCmd | Boiler command / setpoint | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A5 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A5_BlrFlameCmd | BlrFlameCmd | Blr Flame Cmd; Blr=Boiler; Cmd=Command | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 207 | BIO2CONTROLS | UAB2_EC1_B4008_F1A5_BLRFLAMECMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | V | V | value_si = raw VALUE | SENSOR | units=u:volt;V;(m2)(kg)(s-3)(A-1);; | Voltage | 2022-01-08 | present | 151112 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A5_BLRFLAMECMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A5_BLRFLAMECMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A5_BLRFLAMECMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Boiler command / setpoint | u_F1A5_BlrSp | Boiler command / setpoint | setpoint | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A5 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A5_BlrSp | BlrSp | Blr Sp; Blr=Boiler | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 212 | BIO2CONTROLS | UAB2_EC1_B4008_F1A5_BLRSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-08 | present | 151112 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A5_BLRSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A5_BLRSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A5_BLRSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler command / setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Boiler efficiency setpoint | u_F1A5_EffSp | Boiler efficiency setpoint | setpoint | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A5 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A5_EffSp | EffSp | EfficiencySetpoint | Changes heating capacity available to EC or to the shared hot-water loop. | Control parameter requiring verification | Retain for engineering review; include in models only after confirming physical actuator pathway. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 215 | BIO2CONTROLS | UAB2_EC1_B4008_F1A5_EFFSP | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | °F | K | T_K = (VALUE - 32) * 5 / 9 + 273.15 | SENSOR | units=u:fahrenheit;�F;(K);*0.5555555555555556+255.37222222222223; | Temperature | 2022-01-08 | present | 151112 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A5_EFFSP live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, (t.VALUE - 32) * 5 / 9 + 273.15 AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A5_EFFSP t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A5_EFFSP | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Boiler efficiency setpoint. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Fan / VFD speed control | u_F1A5_BlrFanSpd | Fan / VFD speed control | actuator output / position feedback | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | F1A5 | Energy Center boiler/hot-water plant equipment; downstream biome not resolved in inventory. | /UAB2_EC1/B4008_F1A5_BlrFanSpd | BlrFanSpd | Blr Fan Spd; Blr=Boiler; Spd=Speed | Changes airflow, exchange, pressure balance, or mixing for EC. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 206 | BIO2CONTROLS | UAB2_EC1_B4008_F1A5_BLRFANSPD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | Level SENSOR (unit-less) | units=u:null;;;; |  | 2022-01-08 | present | 151112 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_F1A5_BLRFANSPD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_F1A5_BLRFANSPD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_F1A5_BLRFANSPD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes. Inventory category says SENSOR, but point name is control-like; verify whether it is command, setpoint, or actuator feedback.
Pump command | u_FWP12_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | FWP12 | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_FWP12_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 234 | BIO2CONTROLS | UAB2_EC1_B4008_FWP12_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-30 | 1975 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_FWP12_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_FWP12_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_FWP12_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_HWP5A_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | HWP5A | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_HWP5A_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 250 | BIO2CONTROLS | UAB2_EC1_B4008_HWP5A_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 1133 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_HWP5A_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_HWP5A_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_HWP5A_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_HWP5B_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | HWP5B | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_HWP5B_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 252 | BIO2CONTROLS | UAB2_EC1_B4008_HWP5B_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-04 | 945 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_HWP5B_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_HWP5B_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_HWP5B_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_HWP5C_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | HWP5C | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_HWP5C_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 253 | BIO2CONTROLS | UAB2_EC1_B4008_HWP5C_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 369 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_HWP5C_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_HWP5C_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_HWP5C_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Valve command / position | u_SVT2B_VlvCmd | Valve command / position | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | SVT2B | Energy Center hydronic/tower-water valve or loop equipment; downstream loop should be verified. | /UAB2_EC1/B4008_SVT2B_VlvCmd | VlvCmd | Vlv Cmd; Cmd=Command; Vlv=Valve | Changes hydronic/air/water flow through equipment serving EC. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 367 | BIO2CONTROLS | UAB2_EC1_B4008_SVT2B_VLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-04 | 281 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_SVT2B_VLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_SVT2B_VLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_SVT2B_VLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Valve command / position | u_TW_MuVlvCmd | Valve command / position | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | TW | Energy Center hydronic/tower-water valve or loop equipment; downstream loop should be verified. | /UAB2_EC1/B4008_TW_MuVlvCmd | MuVlvCmd | Mu Vlv Cmd; MuVlv=MakeupValve; Cmd=Command; Vlv=Valve | Changes hydronic/air/water flow through equipment serving EC. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 398 | BIO2CONTROLS | UAB2_EC1_B4008_TW_MUVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | VALVE STATUS | trueText=s:OPEN¦falseText=s:CLOSE¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | present | 28928 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_TW_MUVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_TW_MUVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_TW_MUVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Valve command / position | u_TW_ROWtrVlvCmd | Valve command / position | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | TW | Energy Center hydronic/tower-water valve or loop equipment; downstream loop should be verified. | /UAB2_EC1/B4008_TW_ROWtrVlvCmd | ROWtrVlvCmd | Reverse Osmosis Water Valve Command | Changes hydronic/air/water flow through equipment serving EC. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 402 | BIO2CONTROLS | UAB2_EC1_B4008_TW_ROWTRVLVCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | VALVE STATUS | trueText=s:OPEN¦falseText=s:CLOSE¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-03-17 | 711 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_TW_ROWTRVLVCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_TW_ROWTRVLVCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_TW_ROWTRVLVCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Valve command / position. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_TWP15A_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | TWP15A | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_TWP15A_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 369 | BIO2CONTROLS | UAB2_EC1_B4008_TWP15A_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 2992 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_TWP15A_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_TWP15A_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_TWP15A_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_TWP15B_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | TWP15B | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_TWP15B_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 370 | BIO2CONTROLS | UAB2_EC1_B4008_TWP15B_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 4525 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_TWP15B_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_TWP15B_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_TWP15B_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_TWP15C_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | TWP15C | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_TWP15C_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 373 | BIO2CONTROLS | UAB2_EC1_B4008_TWP15C_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-02-04 | 260 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_TWP15C_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_TWP15C_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_TWP15C_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_TWPF9A_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | TWPF9A | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_TWPF9A_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 375 | BIO2CONTROLS | UAB2_EC1_B4008_TWPF9A_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-09 | 6164 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_TWPF9A_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_TWPF9A_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_TWPF9A_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_TWPF9B_PmpCmd | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | TWPF9B | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_TWPF9B_PmpCmd | PmpCmd | Pmp Cmd; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 379 | BIO2CONTROLS | UAB2_EC1_B4008_TWPF9B_PMPCMD | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-05-01 | 4133 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_TWPF9B_PMPCMD live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_TWPF9B_PMPCMD t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_TWPF9B_PMPCMD | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_TWPF9C_PmpCmdOff | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | TWPF9C | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_TWPF9C_PmpCmdOff | PmpCmdOff | Pmp Cmd Off; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 383 | BIO2CONTROLS | UAB2_EC1_B4008_TWPF9C_PMPCMDOFF | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-04-30 | 2073 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_TWPF9C_PMPCMDOFF live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_TWPF9C_PMPCMDOFF t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_TWPF9C_PMPCMDOFF | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Pump command | u_TWPF9C_PmpCmdOn | Pump command | command | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | TWPF9C | Energy Center water-loop pump; downstream loop/biome should be verified by engineers. | /UAB2_EC1/B4008_TWPF9C_PmpCmdOn | PmpCmdOn | Pmp Cmd On; Cmd=Command; Pmp=Pump | Changes water-loop circulation or pressure serving EC or a shared plant loop. | Hydraulic / plant-support control parameter | Use as plant forcing or candidate explanatory variable for water, heat, and air-handling boundary behavior. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 382 | BIO2CONTROLS | UAB2_EC1_B4008_TWPF9C_PMPCMDON | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE |  | raw state | value_si = raw VALUE | DEVICE STATUS/COMMAND | trueText=s:ON¦falseText=s:OFF¦range=E:bacnet:BacnetBinaryPv |  | 2021-10-07 | 2026-03-17 | 1609 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_TWPF9C_PMPCMDON live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_TWPF9C_PMPCMDON t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_TWPF9C_PMPCMDON | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Pump command. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Fan / VFD speed control | u_VFDH1A_Hertz | Fan / VFD speed control | actuator output / position feedback | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | VFDH1A | Energy Center VFD or cooling-tower fan equipment; downstream loop should be verified. | /UAB2_EC1/B4008_VFDH1A_Hertz | Hertz | Hertz | Changes airflow, exchange, pressure balance, or mixing for EC. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 416 | BIO2CONTROLS | UAB2_EC1_B4008_VFDH1A_HERTZ | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | Hz | Hz | value_si = raw VALUE | SENSOR | units=u:hertz;Hz;(s-1);; | Frequency | 2022-05-12 | present | 139219 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_VFDH1A_HERTZ live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_VFDH1A_HERTZ t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_VFDH1A_HERTZ | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Fan / VFD speed control | u_VFDH1A_Rpm | Fan / VFD speed control | actuator output / position feedback | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | VFDH1A | Energy Center VFD or cooling-tower fan equipment; downstream loop should be verified. | /UAB2_EC1/B4008_VFDH1A_Rpm | Rpm | Rpm | Changes airflow, exchange, pressure balance, or mixing for EC. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 419 | BIO2CONTROLS | UAB2_EC1_B4008_VFDH1A_RPM | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | rpm | rpm | value_si = raw VALUE | SENSOR | units=u:revolutions per minute;rpm;(s-1);*0.10471975511965977; | Frequency of rotation | 2022-05-12 | present | 139219 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_VFDH1A_RPM live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_VFDH1A_RPM t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_VFDH1A_RPM | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Fan / VFD speed control | u_VFDH1C_Hertz | Fan / VFD speed control | actuator output / position feedback | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | VFDH1C | Energy Center VFD or cooling-tower fan equipment; downstream loop should be verified. | /UAB2_EC1/B4008_VFDH1C_Hertz | Hertz | Hertz | Changes airflow, exchange, pressure balance, or mixing for EC. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 432 | BIO2CONTROLS | UAB2_EC1_B4008_VFDH1C_HERTZ | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | Hz | Hz | value_si = raw VALUE | SENSOR | units=u:hertz;Hz;(s-1);; | Frequency | 2022-05-12 | present | 139219 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_VFDH1C_HERTZ live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_VFDH1C_HERTZ t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_VFDH1C_HERTZ | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.
Fan / VFD speed control | u_VFDH1C_Rpm | Fan / VFD speed control | actuator output / position feedback | Medium - Energy Center downstream biome unresolved | EC | Inventory BIOMNAME=EC. This is central Energy Center equipment; affected biome is plant-wide or unresolved. | VFDH1C | Energy Center VFD or cooling-tower fan equipment; downstream loop should be verified. | /UAB2_EC1/B4008_VFDH1C_Rpm | Rpm | Rpm | Changes airflow, exchange, pressure balance, or mixing for EC. | Air-exchange boundary-control parameter | Use as known actuator trajectory for ventilation, pressure exchange, or mixing boundary conditions. | Bio2 Controls | Bio2-Controls-Inventory-29Jan2026.xlsx | Table Summary | 434 | BIO2CONTROLS | UAB2_EC1_B4008_VFDH1C_RPM | WHERE TIMESTAMP BETWEEN :t0 AND :t1 ORDER BY TIMESTAMP | TIMESTAMP | VALUE | rpm | rpm | value_si = raw VALUE | SENSOR | units=u:revolutions per minute;rpm;(s-1);*0.10471975511965977; | Frequency of rotation | 2022-05-12 | present | 139219 | Yes - BIO2CONTROLS.UAB2_EC1_B4008_VFDH1C_RPM live-tested in Oracle on 2026-05-02. | SELECT t.TIMESTAMP, t.VALUE AS raw_value, t.VALUE AS value_si FROM BIO2CONTROLS.UAB2_EC1_B4008_VFDH1C_RPM t WHERE t.TIMESTAMP >= DATE '2025-01-01' AND t.TIMESTAMP < DATE '2026-01-01' ORDER BY t.TIMESTAMP; | BIO2CONTROLSALL.UAB2_EC1_B4008_VFDH1C_RPM | Candidate selected from Bio2 Controls inventory because the point name looks like a command, setpoint, actuator output, valve/damper/fan/pump speed, or irrigation handle. Selection family: Fan / VFD speed control. Medium - Energy Center downstream biome unresolved Engineering review should map this central plant point to downstream loops/biomes.

## Output
Physical quantity | Physical symbol | X-coordinate [m] | Y-coordinate [m] | Z-coordinate [m] | Height/depth raw | PDE / inverse-problem role | How it enters PDE or inverse problem | Source system | Inventory file | Inventory sheet | Series ID | Exact source channel name | Oracle table / query path | Oracle selector: dv.sensorid = ... AND dv.variableid = ... | Time column | Value column | Unit raw | Unit canonical | Conversion formula | Location descriptive | Location code | Use in PDE / scientific rationale | Data window start | Data window end | Notes | Ready-to-run SQL (column AA) | Unused | Live-tested in Oracle? | Oracle variable ID from metadata | Oracle variable code | Oracle variable name | Oracle variable units
Physical quantity | Physical symbol | X-coordinate [m] | Y-coordinate [m] | Z-coordinate [m] | Height/depth raw | PDE / inverse-problem role | How it enters PDE or inverse problem | Source system | Inventory file | Inventory sheet | Series ID | Exact source channel name | Oracle table / query path | Oracle selector: dv.sensorid = ... AND dv.variableid = ... | Time column | Value column | Unit raw | Unit canonical | Conversion formula | Location descriptive | Location code | Use in PDE / scientific rationale | Data window start | Data window end | Notes | Ready-to-run SQL (column AA) | Unused | Live-tested in Oracle? | Oracle variable ID from metadata | Oracle variable code | Oracle variable name | Oracle variable units
Air temperature | T(x,t) |  |  | 1 | DLEVEL = 100 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 96 | TRF_MTN_100_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 96 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF Mountain Tower | TRF_MTN | RainForest state measurement at TRF Mountain Tower DLEVEL = 100 cm | 2015-09-21T00:00:00 | present | From RainForest inventory; sensor code: TRF_MTN_100_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 96 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Air temperature | T(x,t) |  |  | 3 | DLEVEL = 300 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 97 | TRF_MTN_300_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 97 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF Mountain Tower | TRF_MTN | RainForest state measurement at TRF Mountain Tower DLEVEL = 300 cm | 2015-09-21T00:00:00 | present | From RainForest inventory; sensor code: TRF_MTN_300_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 97 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Air temperature | T(x,t) |  |  | 7 | DLEVEL = 700 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 98 | TRF_MTN_700_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 98 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF Mountain Tower | TRF_MTN | RainForest state measurement at TRF Mountain Tower DLEVEL = 700 cm | 2015-09-21T00:00:00 | present | From RainForest inventory; sensor code: TRF_MTN_700_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 98 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Air temperature | T(x,t) |  |  | 13 | DLEVEL = 1300 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 99 | TRF_MTN_1300_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 99 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF Mountain Tower | TRF_MTN | RainForest state measurement at TRF Mountain Tower DLEVEL = 1300 cm | 2015-09-21T00:00:00 | present | From RainForest inventory; sensor code: TRF_MTN_1300_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 99 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Relative humidity | RH(x,t) |  |  | 1 | DLEVEL = 100 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 96 | TRF_MTN_100_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 96 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF Mountain Tower | TRF_MTN | RainForest state measurement at TRF Mountain Tower DLEVEL = 100 cm | 2015-09-21T00:00:00 | present | From RainForest inventory; sensor code: TRF_MTN_100_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 96 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %
Relative humidity | RH(x,t) |  |  | 3 | DLEVEL = 300 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 97 | TRF_MTN_300_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 97 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF Mountain Tower | TRF_MTN | RainForest state measurement at TRF Mountain Tower DLEVEL = 300 cm | 2015-09-21T00:00:00 | present | From RainForest inventory; sensor code: TRF_MTN_300_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 97 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %
Relative humidity | RH(x,t) |  |  | 7 | DLEVEL = 700 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 98 | TRF_MTN_700_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 98 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF Mountain Tower | TRF_MTN | RainForest state measurement at TRF Mountain Tower DLEVEL = 700 cm | 2015-09-21T00:00:00 | present | From RainForest inventory; sensor code: TRF_MTN_700_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 98 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %
Relative humidity | RH(x,t) |  |  | 13 | DLEVEL = 1300 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 99 | TRF_MTN_1300_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 99 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF Mountain Tower | TRF_MTN | RainForest state measurement at TRF Mountain Tower DLEVEL = 1300 cm | 2015-09-21T00:00:00 | present | From RainForest inventory; sensor code: TRF_MTN_1300_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 99 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %
Air temperature | T(x,t) |  |  | 1 | DLEVEL = 100 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 42 | TRF_NETower_100_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 42 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF Northeast Tower | TRF_NE | RainForest state measurement at TRF Northeast Tower DLEVEL = 100 cm | 2015-07-23T00:00:00 | present | From RainForest inventory; sensor code: TRF_NETower_100_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 42 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Air temperature | T(x,t) |  |  | 3 | DLEVEL = 300 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 43 | TRF_NETower_300_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 43 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF Northeast Tower | TRF_NE | RainForest state measurement at TRF Northeast Tower DLEVEL = 300 cm | 2015-07-23T00:00:00 | present | From RainForest inventory; sensor code: TRF_NETower_300_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 43 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Air temperature | T(x,t) |  |  | 7 | DLEVEL = 700 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 44 | TRF_NETower_700_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 44 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF Northeast Tower | TRF_NE | RainForest state measurement at TRF Northeast Tower DLEVEL = 700 cm | 2015-07-23T00:00:00 | present | From RainForest inventory; sensor code: TRF_NETower_700_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 44 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Air temperature | T(x,t) |  |  | 13 | DLEVEL = 1300 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 45 | TRF_NETower_1300_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 45 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF Northeast Tower | TRF_NE | RainForest state measurement at TRF Northeast Tower DLEVEL = 1300 cm | 2015-07-23T00:00:00 | present | From RainForest inventory; sensor code: TRF_NETower_1300_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 45 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Air temperature | T(x,t) |  |  | 20 | DLEVEL = 2000 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 46 | TRF_NETower_2000_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 46 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF Northeast Tower | TRF_NE | RainForest state measurement at TRF Northeast Tower DLEVEL = 2000 cm | 2015-07-23T00:00:00 | present | From RainForest inventory; sensor code: TRF_NETower_2000_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 46 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Relative humidity | RH(x,t) |  |  | 1 | DLEVEL = 100 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 42 | TRF_NETower_100_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 42 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF Northeast Tower | TRF_NE | RainForest state measurement at TRF Northeast Tower DLEVEL = 100 cm | 2015-07-23T00:00:00 | present | From RainForest inventory; sensor code: TRF_NETower_100_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 42 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %
Relative humidity | RH(x,t) |  |  | 3 | DLEVEL = 300 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 43 | TRF_NETower_300_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 43 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF Northeast Tower | TRF_NE | RainForest state measurement at TRF Northeast Tower DLEVEL = 300 cm | 2015-07-23T00:00:00 | present | From RainForest inventory; sensor code: TRF_NETower_300_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 43 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %
Relative humidity | RH(x,t) |  |  | 7 | DLEVEL = 700 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 44 | TRF_NETower_700_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 44 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF Northeast Tower | TRF_NE | RainForest state measurement at TRF Northeast Tower DLEVEL = 700 cm | 2015-07-23T00:00:00 | present | From RainForest inventory; sensor code: TRF_NETower_700_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 44 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %
Relative humidity | RH(x,t) |  |  | 13 | DLEVEL = 1300 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 45 | TRF_NETower_1300_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 45 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF Northeast Tower | TRF_NE | RainForest state measurement at TRF Northeast Tower DLEVEL = 1300 cm | 2015-07-23T00:00:00 | present | From RainForest inventory; sensor code: TRF_NETower_1300_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 45 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %
Relative humidity | RH(x,t) |  |  | 20 | DLEVEL = 2000 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 46 | TRF_NETower_2000_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 46 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF Northeast Tower | TRF_NE | RainForest state measurement at TRF Northeast Tower DLEVEL = 2000 cm | 2015-07-23T00:00:00 | present | From RainForest inventory; sensor code: TRF_NETower_2000_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 46 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %
Air temperature | T(x,t) |  |  | 1 | DLEVEL = 100 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 61 | TRF_NWTower_100_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 61 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF Northwest Tower | TRF_NW | RainForest state measurement at TRF Northwest Tower DLEVEL = 100 cm | 2013-12-28T00:00:00 | present | From RainForest inventory; sensor code: TRF_NWTower_100_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 61 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Air temperature | T(x,t) |  |  | 3 | DLEVEL = 300 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 62 | TRF_NWTower_300_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 62 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF Northwest Tower | TRF_NW | RainForest state measurement at TRF Northwest Tower DLEVEL = 300 cm | 2013-12-28T00:00:00 | present | From RainForest inventory; sensor code: TRF_NWTower_300_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 62 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Air temperature | T(x,t) |  |  | 7 | DLEVEL = 700 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 63 | TRF_NWTower_700_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 63 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF Northwest Tower | TRF_NW | RainForest state measurement at TRF Northwest Tower DLEVEL = 700 cm | 2013-12-28T00:00:00 | present | From RainForest inventory; sensor code: TRF_NWTower_700_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 63 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Air temperature | T(x,t) |  |  | 13 | DLEVEL = 1300 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 64 | TRF_NWTower_1300_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 64 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF Northwest Tower | TRF_NW | RainForest state measurement at TRF Northwest Tower DLEVEL = 1300 cm | 2013-12-28T00:00:00 | present | From RainForest inventory; sensor code: TRF_NWTower_1300_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 64 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Relative humidity | RH(x,t) |  |  | 1 | DLEVEL = 100 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 61 | TRF_NWTower_100_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 61 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF Northwest Tower | TRF_NW | RainForest state measurement at TRF Northwest Tower DLEVEL = 100 cm | 2013-12-28T00:00:00 | present | From RainForest inventory; sensor code: TRF_NWTower_100_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 61 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %
Relative humidity | RH(x,t) |  |  | 3 | DLEVEL = 300 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 62 | TRF_NWTower_300_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 62 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF Northwest Tower | TRF_NW | RainForest state measurement at TRF Northwest Tower DLEVEL = 300 cm | 2013-12-28T00:00:00 | present | From RainForest inventory; sensor code: TRF_NWTower_300_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 62 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %
Relative humidity | RH(x,t) |  |  | 7 | DLEVEL = 700 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 63 | TRF_NWTower_700_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 63 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF Northwest Tower | TRF_NW | RainForest state measurement at TRF Northwest Tower DLEVEL = 700 cm | 2013-12-28T00:00:00 | present | From RainForest inventory; sensor code: TRF_NWTower_700_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 63 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %
Relative humidity | RH(x,t) |  |  | 13 | DLEVEL = 1300 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 64 | TRF_NWTower_1300_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 64 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF Northwest Tower | TRF_NW | RainForest state measurement at TRF Northwest Tower DLEVEL = 1300 cm | 2013-12-28T00:00:00 | present | From RainForest inventory; sensor code: TRF_NWTower_1300_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 64 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %
Air temperature | T(x,t) |  |  | 1 | DLEVEL = 100 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 81 | TRF_STower_100_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 81 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF South Tower | TRF_S | RainForest state measurement at TRF South Tower DLEVEL = 100 cm | 2015-09-30T00:00:00 | 2025-09-22T00:00:00 | From RainForest inventory; sensor code: TRF_STower_100_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 81 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Air temperature | T(x,t) |  |  | 3 | DLEVEL = 300 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 82 | TRF_STower_300_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 82 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF South Tower | TRF_S | RainForest state measurement at TRF South Tower DLEVEL = 300 cm | 2015-09-30T00:00:00 | 2025-09-22T00:00:00 | From RainForest inventory; sensor code: TRF_STower_300_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 82 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Air temperature | T(x,t) |  |  | 7 | DLEVEL = 700 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 83 | TRF_STower_700_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 83 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF South Tower | TRF_S | RainForest state measurement at TRF South Tower DLEVEL = 700 cm | 2015-09-30T00:00:00 | 2025-09-22T00:00:00 | From RainForest inventory; sensor code: TRF_STower_700_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 83 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Air temperature | T(x,t) |  |  | 13 | DLEVEL = 1300 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 84 | TRF_STower_1300_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 84 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF South Tower | TRF_S | RainForest state measurement at TRF South Tower DLEVEL = 1300 cm | 2015-09-30T00:00:00 | 2025-09-22T00:00:00 | From RainForest inventory; sensor code: TRF_STower_1300_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 84 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Air temperature | T(x,t) |  |  | 20 | DLEVEL = 2000 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 85 | TRF_STower_2000_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 85 AND dv.variableid = 16 | LOCALDATETIME | DATAVALUE | degC | degC | identity | TRF South Tower | TRF_S | RainForest state measurement at TRF South Tower DLEVEL = 2000 cm | 2015-09-30T00:00:00 | 2025-09-22T00:00:00 | From RainForest inventory; sensor code: TRF_STower_2000_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 85 AND dv.variableid = 16 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 16 | AirTempC | Temperature | degC
Relative humidity | RH(x,t) |  |  | 1 | DLEVEL = 100 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 81 | TRF_STower_100_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 81 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF South Tower | TRF_S | RainForest state measurement at TRF South Tower DLEVEL = 100 cm | 2015-09-30T00:00:00 | 2025-09-22T00:00:00 | From RainForest inventory; sensor code: TRF_STower_100_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 81 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %
Relative humidity | RH(x,t) |  |  | 3 | DLEVEL = 300 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 82 | TRF_STower_300_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 82 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF South Tower | TRF_S | RainForest state measurement at TRF South Tower DLEVEL = 300 cm | 2015-09-30T00:00:00 | 2025-09-22T00:00:00 | From RainForest inventory; sensor code: TRF_STower_300_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 82 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %
Relative humidity | RH(x,t) |  |  | 7 | DLEVEL = 700 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 83 | TRF_STower_700_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 83 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF South Tower | TRF_S | RainForest state measurement at TRF South Tower DLEVEL = 700 cm | 2015-09-30T00:00:00 | 2025-09-22T00:00:00 | From RainForest inventory; sensor code: TRF_STower_700_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 83 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %
Relative humidity | RH(x,t) |  |  | 13 | DLEVEL = 1300 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 84 | TRF_STower_1300_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 84 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF South Tower | TRF_S | RainForest state measurement at TRF South Tower DLEVEL = 1300 cm | 2015-09-30T00:00:00 | 2025-09-22T00:00:00 | From RainForest inventory; sensor code: TRF_STower_1300_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 84 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %
Relative humidity | RH(x,t) |  |  | 20 | DLEVEL = 2000 cm | Pointwise state value constraint | Measured value of the RainForest climate state at observation point (x, z, t); use for calibration, validation, control verification, or data assimilation. | RainForest SensorDB inventory | Bio2-Rainforest-Inventory.xlsx | Sensors | 85 | TRF_STower_2000_HMP45 | BIOMS.DATAVALUES | dv.sensorid = 85 AND dv.variableid = 15 | LOCALDATETIME | DATAVALUE | % | % | identity | TRF South Tower | TRF_S | RainForest state measurement at TRF South Tower DLEVEL = 2000 cm | 2015-09-30T00:00:00 | 2025-09-22T00:00:00 | From RainForest inventory; sensor code: TRF_STower_2000_HMP45 | SELECT dv.LOCALDATETIME, dv.DATAVALUE FROM bioms.DATAVALUES dv WHERE dv.sensorid = 85 AND dv.variableid = 15 ORDER BY dv.LOCALDATETIME |  | Yes — literal AC query validated in Oracle on 2026-05-05. | 15 | RH | Relative humidity | %